| Prepared By (“DSR”): | Prepared For (“Client”): |
| --- | --- |

PRODUCTION SUPERVISION REPORT

For

PV Modules

| Client | : Resolven Private Ltd. |
| --- | --- |
| Project Name | : Ganeko Two Energy Private Ltd. |
| SPV Name | : Solapur Ganeko One Energy Private Ltd. - Shell - 22.9 MWp Solar |

| Report No. | : DSR-PS-RES-2026-10-01 |
| --- | --- |
| Report Date | : 01.10.2026 |
| Manufacturer | : Premier Energies Global Environment Private Ltd. |
| Location | : SY. N:1663 TO 1673, UDL 5/Part, Seetharampur, Telangana 509217 |
| Workshop | : P7 |

TABLE OF CONTENTS

- INSPECTION SUMMARY

- Production Summary

- Non-Conformities

- Report Signatories

- BILL OF MATERIALS (BOM) VERIFICATION

- List of Materials used

- Materials Storage

- PRODUCTION QUALITY CONTROL

- In-Production Quality Control

- Equipment Verification - Sun Simulator

- Tests Witnessing

- Storage of Finished Product

- Manufacturing Data Verification (if applicable)

- Calibration Verification - Sun Simulator

- NON-CONFORMITIES RECORD

- INSPECTION SUMMARY

- Production Summary

- Production Snapshot

| Date | Power Bin | Planned Output |  | Actual Output |  | Deviation |  | Day Shift |  | Night Shift |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Qty. (pcs) | Qty. (MWp) | Qty. (pcs) | Qty. (MWp) | Qty. (pcs) | Qty. (MWp) | Qty. (pcs) | Qty. (MWp) | Qty. (pcs) | Qty. (MWp) |
| 28.09.2026 | 615 Wp | 2000 | 1.23 | 1416 | 0.87 | 584 | -0.36 | 0 | 0 | 1178 | 0.72 |
| 29.09.2026 | 615 Wp | 5000 | 3.08 | 4120 | 2.53 | 880 | -0.54 | 1829 | 1.12 | 1860 | 1.14 |
| 30.09.2026 | 615 Wp | 4600 | 2.83 | 3912 | 2.41 | 688 | -0.42 | 1829 | 1.12 | 1860 | 1.14 |
| 01.10.2026 | 615 Wp | 4600 | 2.83 | 4310 | 2.65 | 290 | -0.18 | 1860 | 1.14 | 2201 | 1.35 |
| Total: |  | 16200 | 9.96 | 13758 | 8.46 | 2442 | -1.50 | 5518 | 3.39 | 7099 | 4.36 |

- Production Status - Qualified & Rejected Modules

| Power Bin | 610 Wp Qualified |  | 615 Wp Qualified |  | Module YTD |  | Rejected |  | EL Rework Rejected |  | Suspected Qty. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date | Qty. (pcs) | Qty. (MWp) | Qty. (pcs) | Qty. (MWp) | Qty. (pcs) | Qty. (MWp) | Qty. (pcs) | Qty. (MWp) | Qty. (pcs) | Qty. (MWp) | Qty. (pcs) | Qty. (MWp) |
| 01.10.2026 | 0 | 00 | 4061 | 2.50 | 4061 | 2.50 | 42 | 0.03 | 14 | 0.01 | 164 | 0.10 |
| Cumulative Production | 0 | 00 | 12617 | 7.76 | 12617 | 7.76 | 114 | 0.07 | 57 | 0.04 | 290 | 0.18 |

- Non-Conformities

| Workshop/ Line | Date of Finding | Description | Severity | Process | No. of Affected Modules | Control Type | Vendor Immediate Action Containment | Closure Status |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 07/02 | 01.10.2026 | The cell peel test for Stringer 5 failed during the second trial on 30th September | Major | Stringer | 164 | Auto | Status Pending | Open |
| / | / | / | / | / | / | / | / | / |

- Report Signatories

| PREPARED BY | PROJECT ENGINEER |  |
| --- | --- | --- |
| REVIEWED BY | REPORT AUDITOR |  |
| APPROVED BY | TECHNICAL MANAGER |  |

- BILL OF MATERIALS (BOM) VERIFICATION

LINE 1 & 2 - Day Shift

- List of Materials used

| Material Name | Make & Models |  | Country of Origin |  | Batch No. | Results | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | As per BOM | As per Actual | As per BOM | As per Actual |  |  |  |
| Solar Cell | PT. Bintan (G12R-A-16BB) | PT. Bintan (G12R-A-16BB)) | Indonesia | Indonesia | A260707NP219363 | Pass | Nil |
| Front Cover (Front Glass) | Anhui CSG 2376 x 1128 x 2.0mm | Anhui CSG 2376 x 1128 x 2.0mm | China | China | POAH2604519158 | Pass | Nil |
| Back Cover (Rear Glass) | Anhui CSG 2376 x 1128 x 2.0mm | Anhui CSG 2376 x 1128 x 2.0mm | China | China | POAH2604524830 | Pass | Nil |
| Encapsulation (Front Side) | Hangzhou First, EP304 Unit Weight: ≥ 460gm/m² | Hangzhou First, EP304 Unit Weight: ≥ 460gm/m² | China | China | AE16231-25 | Pass | Nil |
| Encapsulation (Rear Side) | Hangzhou First, EP308 Unit Weight: ≥ 460gm/m² | Hangzhou First, EP308 Unit Weight: ≥ 460gm/m² | China | China | AE35314-17 | Pass | Nil |
| Frame Parts | Jiangyin Haihong (Tinze) 6005-T6, L: 2382 x 35 x 35mm S: 1134 x 35 x 35mm 6005-T6, L: 2382 x 35 x 35mm S: 1134 x 35 x 35mm | Jiangyin Haihong (Tinze) 6005-T6, L: 2382 x 35 x 35mm S: 1134 x 35 x 35mm 6005-T6, L: 2382 x 35 x 35mm S: 1134 x 35 x 35mm | China | China | L-210807A20 S-210807B20 | Pass | Nil |
| Junction Box | QC Solar, 3Qxy,3 Nos., 1500 Vdc, 30 Amp, IP 68 | QC Solar, 3Qxy, 3 Nos., 1500 Vdc, 30 Amp, IP 68 | China | China | QC260824-X171 | Pass | Nil |
| Cable + Connector | QC Solar, 1C x 4mm2, 1500 Vdc, QC4.10 cds, 41 Amp, IP 68 Cable Length: 400 mm (Including Connector) | QC Solar, 1C x 4mm2, 1500 Vdc, QC4.10 cds, 41 Amp, IP 68 Cable Length: 400 mm (Including Connector) | China | China | QC260824-X171 | Pass | Nil |
| Bypass Diode | QC Solar, 3 Nos., QCM5045B, 45V, 50A | QC Solar, 3 Nos., QCM5045B, 45V, 50A | China | China | QC260824-X171 | Pass | Nil |
| Cell Connector | TaiCang JuRen PV Material, 0.24mm, Round, Tin Plated, Sn:60%, Pb:40% | TaiCang JuRen PV Material, 0.24mm, Round, Tin Plated, Sn:60%, Pb:40% | China | China | BFG1610350008115 | Pass | Nil |
| String Connector | TaiCang JuRen PV Material, 0.35 x 4mm /0.35 x 6mm, Tin Plated, Sn:60%, Pb:40% | TaiCang JuRen PV Material, 0.4 x 4mm /0.4 x 6mm, Tin Plated, Sn:60%, Pb:40% | China | China | BFHZV2540007210 BFHZS2586010209 | Pass | First 50MW |
| Adhesive (Frame) | Guangzhou Baiyun SMG-533 | Guangzhou Baiyun SMG-533 | China | China | G260729C3302 | Pass | Nil |
| Adhesive (JB) | Guangzhou Baiyun SMG-533 | Guangzhou Baiyun SMG-533 | China | China | G260729C3302 | Pass | Nil |
| Potting Material (Junction Box) | Guangzhou Baiyun SKF0323 (A & B) | Guangzhou Baiyun SKF0323 (A & B) | China | China | G260817B2301 G260815A1501 | Pass | Nil |
| Fluxing Agent | Shenzen Glory Flux 8000T20 | HUAI HUI Flux 8000T20 | China | China | HH20260521-DA | Pass | Nil |
| Fixing Tape | Cybrid FF-3665 | Cybrid FF-3665 | China | China | 251228232008 | Pass | Nil |

- Materials’ Pictures

| Solar Cell - Box Label | Solar Cell - Cassette Label | Solar Cell - Front |
| --- | --- | --- |
| Solar Cell - Rear | Cell Connector - Label on the Box | Cell Connector - Label on the Roll |
| String Connector - Label on the Box | String Connector - Label on the Roll | Front Glass |
| Back Glass | EPE (Front Side) – Label on Package & Roll | EPE (Rear Side) – Label on Package & Roll |
| Frame - Label on Package (Long Frame) | Frame - Label on Package (Short Frame) | Adhesive Sealant (Frame) - Label |
| JB Adhesive Sealant – Label on Package | Complete Junction Box + Cable | JB Potting Material – Label on Package Part -A |
| JB Potting Material – Label on Package Part -B | Flux - Label on Container | Fixing Tape - Label inside Roll |

- Materials Storage Conditions

| Material | Temperature (°C) | Humidity (%) | Expiry Date (if Required) | Observations | Results | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Solar Cell | 25.5 | 56 | Nil | Nil | Pass | Nil |
| Front Glass | 26.3 | 55 | Nil | Nil | Pass | Nil |
| Back Glass | 26.3 | 55 | Nil | Nil | Pass | Nil |
| EPE & EPE | 25.5 | 56 | Nil | Nil | Pass | Nil |
| Frame Parts | 22.7 | 47 | Nil | Nil | Pass | Nil |
| Cell Connector | 26.3 | 55 | Nil | Nil | Pass | Nil |
| String Connector | 26.3 | 55 | Nil | Nil | Pass | Nil |
| Adhesive (Frame) | 25.5 | 56 | Nil | Nil | Pass | Nil |
| Junction Box | 26.3 | 55 | Nil | Nil | Pass | Nil |
| Adhesive (Junction Box) | 25.5 | 56 | Nil | Nil | Pass | Nil |
| Potting Material | 25.5 | 56 | Nil | Nil | Pass | Nil |
| Fluxing Agent | 25.5 | 56 | Nil | Nil | Pass | Nil |
| Fixing Tape | 26.3 | 55 | Nil | Nil | Pass | Nil |

- Material Storage Pictures

| Solar Cell | Front Glass | Rear Glass |
| --- | --- | --- |
| EPE (Front) | EPE (Back) | Junction Box |
| Cells Connector | Strings Connector | Adhesive & Potting Material |
| Fluxing Agent | Potting Material | Frame Parts |

Line –1 & 2 - Night Shift

- List of Materials used

| Material Name | Make & Models |  | Country of Origin |  | Batch No. | Results | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | As per BOM | As per Actual | As per BOM | As per Actual |  |  |  |
| Solar Cell | PT. Bintan (G12R-A-16BB) | PT. Bintan (G12R-A-16BB)) | Indonesia | Indonesia | A260717NP295727 | Pass | Nil |
| Front Cover (Front Glass) | Anhui CSG 2376 x 1128 x 2.0mm | Anhui CSG 2376 x 1128 x 2.0mm | China | China | POAH2604519740 | Pass | Nil |
| Back Cover (Rear Glass) | Anhui CSG 2376 x 1128 x 2.0mm | Anhui CSG 2376 x 1128 x 2.0mm | China | China | POAH2604524879 | Pass | Nil |
| Encapsulation (Front Side) | Hangzhou First, EP304 Unit Weight: ≥ 460gm/m² | Hangzhou First, EP304 Unit Weight: ≥ 460gm/m²² | China | China | AE34293-58 | Pass | Nil |
| Encapsulation (Rear Side) | Hangzhou First, EP308 Unit Weight: ≥ 460gm/m² | Hangzhou First, EP308 Unit Weight: ≥ 460gm/m² | China | China | AE35314-16 | Pass | Nil |
| Frame Parts | Jiangyin Haihong (Tinze) 6005-T6, L: 2382 x 35 x 35mm S: 1134 x 35 x 35mm | Jiangyin Haihong (Tinze) 6005-T6, L: 2382 x 35 x 35mm S: 1134 x 35 x 35mm | China | China | L-210807A20 S-210807B20 | Pass | Nil |
| Junction Box | QC Solar, 3Qxy,3 Nos., 1500 Vdc, 30 Amp, IP 68 | QC Solar, 3Qxy, 3 Nos., 1500 Vdc, 30 Amp, IP 68 | China | China | QC260824-X647 | Pass | Nil |
| Cable + Connector | QC Solar, 1C x 4mm2, 1500 Vdc, QC4.10 cds, 41 Amp, IP 68 Cable Length: 400 mm (Including Connector) | QC Solar, 1C x 4mm2, 1500 Vdc, QC4.10 cds, 41 Amp, IP 68 Cable Length: 400mm (Including Connector) | China | China | QC260824-X647 | Pass | Nil |
| Bypass Diode | QC Solar, 3 Nos., QCM5045B, 45V, 50A | QC Solar, 3 Nos., QCM5045B, 45V, 50A | China | China | QC260824-X647 | Pass | Nil |
| Cell Connector | TaiCang JuRen PV Material, 0.24mm, Round, Tin Plated, Sn:60%, Pb:40% | TaiCang JuRen PV Material, 0.24mm, Round, Tin Plated, Sn:60%, Pb:40% | China | China | BFH0310666053102 | Pass | Nil |
| String Connector | TaiCang JuRen PV Material, 0.35 x 4mm /0.35 x 6mm, Tin Plated, Sn:60%, Pb:40% | TaiCang JuRen PV Material, 0.4 x 4mm /0.4 x 6mm, Tin Plated, Sn:60%, Pb:40% | China | China | BFHZV2540007504 BFHZE1263012202 | Pass | First 50MW |
| Adhesive (Frame) | Guangzhou Baiyun SMG-533 | Guangzhou Baiyun SMG-533 | China | China | G260730C3362 | Pass | Nil |
| Adhesive (JB) | Guangzhou Baiyun SMG-533 | Guangzhou Baiyun SMG-533 | China | China | G260730C3362 | Pass | Nil |
| Potting Material (Junction Box) | Guangzhou Baiyun SKF0323 (A & B) | Guangzhou Baiyun SKF0323 (A & B) | China | China | G260817B2379 G260815A1501 | Pass | Nil |
| Fluxing Agent | Shenzen Glory Flux 8000T20 | Huai Hui Flux 8000T20 | China | China | HH20260521-DA | Pass | Nil |
| Fixing Tape | Cybrid FF-3665 | Cybrid FF-3665 | China | China | 251228232008 | Pass | Nil |

- Material’s Pictures

| Solar Cell - Box Label | Solar Cell - Cassette Label | Solar Cell - Front |
| --- | --- | --- |
| Solar Cell - Rear | Cell Connector - Label on the Box | Cell Connector - Label on the Roll |
| String Connector - Label on the Box | String Connector - Label on the Roll | Front Glass |
| Back Glass | EPE (Front Side) – Label on Package & Roll | EPE (Rear Side) – Label on Package & Roll |
| Frame - Label on Package (Long Frame) | Frame - Label on Package (Short Frame) | Adhesive Sealant (Frame) - Label |
| JB Adhesive Sealant – Label on Package | Complete Junction Box + Cable | JB Potting Material – Label on Package Part -A |
| JB Potting Material – Label on Package Part -B | Flux - Label on Container | Fixing Tape - Label inside Roll |

- Materials Storage Conditions

| Material | Temperature (°C) | Humidity (%) | Expiry Date (if Required) | Observations | Results | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Solar Cell | / | / | Nil | Nil | Pass | Nil |
| Front Glass | / | / | Nil | Nil | Pass | Nil |
| Back Glass | / | / | Nil | Nil | Pass | Nil |
| EPE & EPE | / | / | Nil | Nil | Pass | Nil |
| Frame Parts | / | / | Nil | Nil | Pass | Nil |
| Cell Connector | / | / | Nil | Nil | Pass | Nil |
| String Connector | / | / | Nil | Nil | Pass | Nil |
| Adhesive (Frame) | / | / | Nil | Nil | Pass | Nil |
| Junction Box | / | / | Nil | Nil | Pass | Nil |
| Adhesive (Junction Box) | / | / | Nil | Nil | Pass | Nil |
| Potting Material | / | / | Nil | Nil | Pass | Nil |
| Fluxing Agent | / | / | Nil | Nil | Pass | Nil |
| Fixing Tape | / | / | Nil | Nil | Pass | Nil |

- Material Storage Pictures

| Solar Cell | Front Glass | Rear Glass |
| --- | --- | --- |
| Warehouse was closed during the night shift. | Warehouse was closed during the night shift. | Warehouse was closed during the night shift. |
| EPE (Front) | EPE (Back) | Junction Box |
| Warehouse was closed during the night shift. | Warehouse was closed during the night shift. | Warehouse was closed during the night shift. |
| Cells Connector | Strings Connector | Adhesive & Potting Material |
| Warehouse was closed during the night shift. | Warehouse was closed during the night shift. | Warehouse was closed during the night shift. |
| Fluxing Agent | Potting Material | Frame Parts |
| Warehouse was closed during the night shift. | Warehouse was closed during the night shift. | Warehouse was closed during the night shift. |

- PRODUCTION QUALITY CONTROL

- In-Production Quality Control

| Process | IPQC Process | Equipment Settings & Parameters | Qty. Tested /Inspected | Test Results | Inspection Results | Workshop /Line | Remarks |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Materials Usage | IPQC.01 Material Usage - Bill of Materials | As per approved BOM by Buyer, no deviations allowed | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Solar Cell | IPQC.02 Solar Cell - Visual Inspection | As per Visual – QAP | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Solar Cell | IPQC.02 Solar Cell - Colour Grading | Colour grading shall be such that no colour jumping in single module. | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Solar Cell | IPQC.02 Solar Cell - Usage Validity after Unboxing | Usage within 24 Hrs. | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Solar Cell | IPQC.02 Solar Cell -Storage Conditions | Environmental condition shall be as per Solar cell section - Incoming Material | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Cell Cutting for Half Cut Cell | IPQC.03 Cell Cutting for Half Cut Cell - Visual Check | No cutting residues | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Cell Cutting for Half Cut Cell | IPQC.03 Cell Cutting for Half Cut Cell - EL Imaging | To be as per EL Criteria | 10 | No effect | Pass | Line-01&02 | Strings Verified at Stringer EL |  |
| Cell Cutting for Half Cut Cell | IPQC.03 Cell Cutting for Half Cut Cell - Cell Cutting Method | To be as per Annexure | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Front EPE Cutting | IPQC.04 Front EPE Cutting - Cutting Size | As per material vendor requirements | 10 | 2376*1123 mm | Pass | Line-01&02 | Nil |  |
| Back EPE Cutting | IPQC.04 Back EPE Cutting - Cutting Size | As per material vendor requirements | 10 | 2377*1123 mm | Pass | Line-01&02 | Nil |  |
| EPE Cutting | IPQC.04 EPE Cutting - Usage Validity after Unboxing | Usage within 6 hrs. for normal production module and for rework module, usage within 12 Hrs. | 10 | No effect | Pass | Line-01&02 | Nil |  |
| EPE Cutting | IPQC.04 EPE Cutting - Storage Conditions | Environmental condition shall be as per EPE Section. Incoming Material - QAP | 10 | Temperature: 24.7℃, Humidity: 42.4% | Pass | Line-01&02 | Within Range |  |
| Glass (Front) | IPQC.05 Front Glass Size | As per Approved BOM | 10 | 2376*1128*2.0mm | Pass | Line-01&02 | Nil |  |
| Glass (Back) | IPQC.05 Back Glass Size | As per Approved BOM | 10 | 2376*1128*2.0mm | Pass | Line-01&02 | Nil |  |
| Glass (Front & Back) | IPQC.05 Glass - Storage Conditions | Environmental conditions shall be as per the Glass Section. Incoming - QAP | 10 | Temperature: 24.7℃, Humidity: 42.4% | Pass | Line-01&02 | Nil |  |
| Stringing | IPQC.06 Stringing - Peel Strength Test of Stringing (Front Side and Back Side of Cell) | 5 Pad value must be greater than 0.80 N and no point on pad should be less than 0.5N joints meet the standard requirement. | 192Sets | Front: 3.06N Back: 2.42N | Pass | Line-01&02 | Nil |  |
| Stringing | IPQC.06 Stringing - Space between Cells, Space between Strings | As per Visual - QAP | 10 | C to C: 0.81 mm S to S: 1.62 mm | Pass | Line-01&02 | Nil |  |
| Stringing | IPQC.06 Stringing - Temperature Settings and Inspection of Soldering Equipment | As per Manufacturer technical requirements | 10 | 111.0℃ | Pass | Line-01&02 | Nil |  |
| Layup | IPQC.07 Layup - Space between Strings | As per Visual - QAP | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Layup | IPQC.07 Layup - Insulation Assembly | Correct Dimensions and positioning, no short Circuit risk and wrinkle | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Layup | IPQC.07 Layup - Cell Arrangement and Interconnection | As per Manufacturer technical drawing | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Layup | IPQC.07 Layup - Tensile welding force of Busbar and Interconnection | To be as per Annexure (≥2.0N) | 10 | 2.89 N | Pass | Line-01&02 | Nil |  |
| Lamination | IPQC.08 Lamination - EL before Lamination | As per EL Criteria | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Lamination | IPQC.08 Lamination - Visual Check before Lamination | As per Visual - QAP | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Lamination | IPQC.08 Lamination - Serial Number Label Inspection | Serial Number Label Position and No Wrinkle | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Lamination | IPQC.08 Lamination - Visual Check after Lamination | As per Visual - QAP | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Lamination | IPQC.08 Lamination - Lamination Parameters | As per Manufacturer Technical Specifications defined for each Encapsulant and the laminator condition | 10 | 146°C | Pass | Line-01&02 | Nil |  |
| Lamination | IPQC.08 Lamination- Lamination Sensor Calibration | As per Machine technical Specifications | 10 | No effect | Pass | Line-01&02 | Nil |  |
| Lamination | IPQC.08 Lamination - Peel strength between Front Glass and EPE | To be as per Annexure (>70N/cm) | 2 | LAM-2U9: 165.03 N/cm | Pass | Line-01&02 | Nil |  |
| Lamination | IPQC.08 Lamination - Peel strength between Back Glass and EPE | To be as per Annexure (>70N/cm) | 1 | LAM-2L7: 159.58 N/cm LAM-3L3: 148.25 N/cm | Pass | Line-01&02 |  | Nil |
| Lamination | IPQC.08 Lamination - Gel Content Test | To be as per Annexure (EPE.:80 - 95%) | 3 | LAM-2L7: 89.05% LAM-2U9: 87.54 % LAM-3L3: 88.82 % | Pass | Line-01&02 |  | Nil |
| Frame Marking | IPQC.09 Identification Marking - Sign Marking | 100% marking on frame Pallets/Packets should be done | 100% | Not Applicable | N/A | Line-01&02 |  | Nil |
| Edge Trimming and Framing | IPQC.09 Edge Trimming and Framing - Trimming Quality | No Extra Overhang of Encapsulant outside frame | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Edge Trimming and Framing | IPQC.09 Edge Trimming and Framing - Trimming Tool Replacement | As per manufacturer criteria of tool maintenance | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Edge Trimming and Framing | IPQC.09 Edge Trimming and Framing - Visual Check | As per Visual - QAP | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Edge Trimming and Framing | IPQC.09 Edge Trimming and Framing - Adhesive Sealant and Deposition Quality | Good uniformity, no overflow and no gaps allowed Sealant must be filled in frame before fixing, and after framing no additional sealant to be applied on module | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Edge Trimming and Framing | IPQC.09 Edge Trimming and Framing -Dimensions, Holes and Frame Profile | As per technical specifications approved by Buyer, no deviation Allowed | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Junction Box Assembly | IPQC.10 Junction Box Assembly - Position | As per technical specifications of manufacturer | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Junction Box Assembly | IPQC.10 Junction Box Assembly - Adhesive Sealant Specifications | As per Sealant technical Specifications, Proper A:B ratio of sealant (6±0.8:1) | 5 | 6.01:1 | Pass | Line-01&02 |  | Nil |
| Junction Box Assembly | IPQC.10 Junction Box assembly - Junction Box Soldering Specifications and Quality | To be as per Annexure | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Junction Box Assembly | IPQC.10 Junction Box Assembly - Operator Safety | Operators must wear ESD wrist strip | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Curing | IPQC.11 Curing - Ambient Temperature and Humidity | Temperature: 25±3°C, Humidity: >70%RH | 10 | Temperature: 25.0℃, Humidity: 73.4% | Pass | Line-01&02 |  | Nil |
| Curing | IPQC.11 Curing - Stacking of Modules | Stacking of modules to be done in such a way that each module gets proper ventilation for Sealant/Potent drying in the curing time. | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Curing | IPQC.11 Curing - Curing Time | Time 4.5 Hrs. | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Final Testing | Calibration of Gold Module and Storage | Verification, calibration and actual power determination of Gold module. Storage in dark room with 25±2°C Zero Crack determination by EL. | 6 | Temperature: 24.5℃, Humidity: 45% | Pass | Line-01&02 |  | Nil |
| Final Testing | Verification of Temperature & Irradiance Factors for Flash Test | As approved by Buyer, No deviations allowed | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Final Testing | Ambient Temperature and Humidity | Temperature 25±2°C, Humidity ≤60% | 10 | Temperature: 24.5℃, Humidity:45% | Pass | Line-01&02 |  | Nil |
| Final Testing | Ground Continuity Test | Apply 75A Current for 2S, Test resistance should be <100mΩ. | 10 | 1.825 mΩ | Pass | Line-01&02 |  | Nil |
| Final Testing | High Voltage Test (Hi-Pot) | Test Condition: Voltage 4800V during 2S, Requirement: Current Leakage ≤50µA | 10 | 1.3 uA | Pass | Line-01&02 |  | Nil |
| Final Testing | Insulation Resistance Test | Voltage 1500 Vdc, Insulation Resistance > 1000MΩ, Test Time is 2S. | 10 | 4.713 GΩ | Pass | Line-01&02 |  | Nil |
| Final Testing | Electroluminescence Test | As per EL Criteria in Annexure | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Final Testing | Module Sr. No. & Back Label | As approved by Buyer, No deviations allowed. | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Final Testing | Current Sorting | To be as per Annexure | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Final Testing | RFID Label/Barcode Scanning | The label is attached in the correct position, no bubbles. Data should be accurate. | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Final Testing | Flash Test for Front Side | To be as per Annexure | 10 | No effect | Pass | Line-01&02 |  | Nil |
| Module Packing | 31 Modules/Pallet | To be checked as per Packaging Manual | 10 | No effect | Pass | Line-01&02 |  | Nil |

- Equipment Verification - Sun Simulator

- Flasher Verification

| Equipment Make/ Type | Equipment Number# | Equipment Class | Verification Date | Equipment Calibration/ Test Date | Cable Connector Usage (No. of Ops.*) | Lamp Usage (No. of Ops.*) | Room Temperature (°C) | Temperature of Reference Cell (°C) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G SOLAR GIV-20A2616 | GS20A261626010222 (Line-1) | A+A+A+ | 01.10.2026 | 11.03.2026 | / | 42879 | 25.68°C | 26.13°C |
| G SOLAR GIV-20A2616 | GS20A261626010123 (Line-2) | A+A+A+ | 01.10.2026 | 11.03.2026 | / | 55683 | 24.50°C | 25.85°C |

- Flasher Test Results

| Equipment Number# | 1st Reference Module Serial Number | Flash Date & Time | Reff. Pmpp (Wp) | Actual Pmpp (Wp) | Deviations (%) | Inspection Method | I-V Curve Verification | EL Check |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GS20A261626010123 (Line-1) | NSMS26050001569 | 01.10.2026 06:12 AM | 610.27 | 609.52 | -0.12% | Witness | Pass | Pass |
| GS20A261626010123 (Line-1) | NSMS26050001569 | 01.10.2026 09:50 AM | 610.27 | 608.09 | -0.36% | Witness | Pass |  |
| GS20A261626010123 (Line-1) | NSMS26050001569 | 01.10.2026 02:00 PM | 610.27 | 608.27 | -0.31% | Witness | Pass |  |
| GS20A261626010123 (Line-1) | NSMS26050001569 | 01.10.2026 06:03 PM | 610.27 | 607.45 | -0.46% | Witness | Pass |  |
| GS20A261626010123 (Line-1) | NSMS26050001569 | 01.10.2026 10:02 PM | 610.27 | 608.27 | -0.31% | Witness | Pass |  |
| GS20A261626010123 (Line-1) | NSMS26050001569 | 02.10.2026 02:12 AM | 610.27 | 608.39 | -0.31% | Witness | Pass |  |
| GS20A261626010222 (Line-2) | NSMG26060493685 | 02.10.2026 01:36 AM | 609.67 | 610.02 | 0.06% | Witness | Pass | Pass |

- Sun Simulator Verification Pictures

| Equipment Picture | Connectors | Reference Module Storage |
| --- | --- | --- |
| Temperature and Humidity Control | Equipment Calibration Certificate (Line-1) | Equipment Calibration Certificate (Line-2) |

- Tests Witnessing

- Soldering Peel Off (Avg. value)

| Line | Shift | Date | Front Soldering Test |  |  |  |  |  |  | Rear Soldering Test |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| 1 | Day | 01.10.2026 | 2.13 | 3.18 | 3.08 | 3.11 | 3.13 | 3.39 | 2.34 | 2.70 | 3.44 | 3.78 | 3.48 | 3.64 | 2.61 | 1.64 |
| 1 | Night | 01.10.2026 | 2.50 | 3.52 | 3.51 | 3.28 | 3.34 | 3.20 | 3.05 | 3.08 | 2.28 | 2.28 | 2.66 | 2.56 | 2.64 | 2.07 |
| 2 | Day | 01.10.2026 | 2.52 | 2.96 | 3.16 | 3.07 | 3.33 | 3.70 | 2.79 | 3.26 | 3.22 | 3.27 | 3.33 | 3.41 | 2.97 | 2.54 |
| 2 | Night | 01.10.2026 | 2.33 | 3.22 | 3.35 | 2.94 | 3.44 | 3.78 | 2.73 | 3.13 | 2.15 | 2.13 | 2.44 | 2.43 | 3.05 | 2.97 |

- Encapsulation Cross-Link or Gel Content (80% - 95%)

| Line | Shift | Laminator No. | Sample-1 | Sample-2 | Sample-3 | Sample-4 | Sample-5 | Gel Content (%) | Results | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2 | A | LAM-2L7 | 89.45% | 88.87% | 87.77% | 89.74% | 89.41% | 89.05% | Pass | - |
| 2 | A | LAM-2U9 | 86.18% | 89.20% | 88.51% | 88.43% | 85.39% | 87.54% | Pass |  |
| 2 | B | LAM-3L3 | 89.10% | 88.74% | 87.80% | 89.90% | 88.57% | 88.82% | Pass | - |
| Overall Result |  |  |  |  |  |  |  |  | Pass |  |

- Dimension Check

| Module Serial Number | Length (mm) | Width (mm) | Diagonal (mm) | Distance Between Mounting Holes-1 (mm) | Distance Between Mounting Holes-2 (mm) | Distance Between Mounting Holes-3 (mm) | Distance Between Mounting Holes (Width Wise) (mm) | Cable Length (mm) | Frame Dim. (mm) | Results |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Standard Values | 2382±2 | 1134±2 | 2638±2 | 1400±1 | 790±1 | 400±1 | 1084±2 | 400+10 | (35×35) | Pass /Fail |
| NSME26090127282 | 2382 | 1134 | 2638 | 1401 | 791 | 400 | 1085 | 400 | (35×35) | Pass |
| NSME26090124459 | 2382 | 1134 | 2637 | 1400 | 790 | 400 | 1084 | 402 | (35×35) | Pass |
| Overall Result |  |  |  |  |  |  |  |  | Pass |  |

- RFID Check

| Module Sr. No. | Shift | Module Type | Solar Cell | Pmax | Voc | Isc | Vmp | Imp | FF (%) | Certification | Results |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| NSME26090127542 | Day | PE-132-615THGB-G12R | PT Bintan | 620.12 | 48.72 | 15.73 | 41.19 | 15.05 | 80.89 | TUV | PASS |
| NSME26100002012 | Night | PE-132-615THGB-G12R | PT Bintan | 620.30 | 48.85 | 15.74 | 41.28 | 15.02 | 80.63 | TUV | PASS |

- Recorded Pictures

| Reference Dimensions | Soldering Peel-Off Test | Soldering Peel-Off Test Data |
| --- | --- | --- |
| Gel Content Test | Gel Content Oven | Dimension Check Witness |
| Dimension Check Witness | Dimension Check Witness | Dimension Check Witness |
| Dimension Check Witness | Dimension Check Witness | Dimension Check Witness |
| Dimension Check Witness | Module Label Marking-1 (615Wp) | Polarity (Junction Box) Marking-1 |
| RFID Check | RFID Check | RFID Check |

- Internal Lab Tests

| Module Sr. No. | Item/Property Measured | Method Used | Checks/Acceptance Limit | Qty. Inspected | Results |
| --- | --- | --- | --- | --- | --- |
| / | PID Test | / | / | / | / |
| / | LETID Test | / | / | / | / |
| / | LID Test | / | / | / | / |

- Recorded Pictures

| PID Test | PID Test | PID Test |
| --- | --- | --- |
| N/A | N/A | N/A |
| LETID Test | LETID Test | LETID Test |
| N/A | N/A | N/A |
| LID Test | LID Test | LID Test |
| N/A | N/A | N/A |

- Finished Product Storage

| Storage Area | Product Stored | Inspection Time | Products and Packaging Conditions | Storage Conditions | Inspection Results | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Warehouse | PE-132-615THGB-G12R | 01.10.2026 3.50 PM | PASS | Indoor | Pass | Nil |
| Warehouse | PE-132-615THGB-G12R | 02.10.2026 3:40 AM | PASS | Indoor | Pass | Nil |

| Warehouse Overall Condition | Pallet Stacking | Packing List |
| --- | --- | --- |

- Manufacturing Data Verification (if applicable)

- Manufacturing Data Collection, Verification & Sampling

| Date of Production | Data Collected | Qty. Collected (Nos.) | Data Verification for Consistency | Non-Conformities in Data (Nos.) | Sampled Data (Nos.) | Sampled Data Results | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 01.10.2026 | Visual | 4061 | Nil | Nil | 36 | Pass | Nil |
| 01.10.2026 | Flash Test | 4061 | Nil | Nil | 36 | Pass | Nil |
| 01.10.2026 | EL Check | 4061 | Nil | Nil | 406 | Under Review | Nil |

- Sun-Simulator Calibration Verification

- Basic Information

| Description | Values |
| --- | --- |
| 1st Reference Module Serial Number | NSMG26060493685, NSMS26050001569 |
| Reference Module Usage Workshop & Line | Workshop-07, Line-01&02 |
| Verification of Sun Simulator with Gold Module | Every 4 Hrs. |
| Frequency of Calibration/Validation with Gold Module | NA |
| Silver Module Verification with Gold Module | NA |
| Power Variation Tolerance Standard | Pmpp Deviation Calibration ≤±0.25% Validation-≤±0.60% |
| Equipment Serial Number | GS20A26162601022, GS20A261626010123 |
| Equipment Class | A+A+A+ |
| Equipment Settings Reference Standard | IEC 60904-9:2020 |
| Software Parameters Settings for Temperature Coefficients | Isc: +0.045%/℃, VOC: -0.25%/℃ |
| Cable Connectors Maintenance | N/A |
| Lamp Usage Maintenance | 100000 |

- Sun-Simulator Calibration Verification

Reference Modules Data:

| Reference Module | 1st Reference (Line-1) | 1st Reference (Line-2) |
| --- | --- | --- |
| Test Report Number | TC1326726000000512F | TC1326726000000622F |
| Test Report Date | 02-06-2026 | 29-06-2026 |
| Test Report Issued By | TUV | TUV |
| Pre-Conditioning Conditions | Ok | Ok |
| Reference - Product Type | Ok | Ok |
| BOM Consistency with Order | Ok | Ok |
| I-V Curve Verification | Ok | Ok |
| EL Picture Review | Ok | Ok |
| Temperature of PV Module (°C) | 25°C | 25°C |
| Pmpp (Wp) | 610.27 | 609.67 |
| Vmpp(V) | 41.05 | 41.02 |
| Impp(A) | 14.87 | 14.87 |
| Voc (V) | 48.62 | 48.53 |
| Isc (A) | 15.62 | 15.63 |
| Fill Factor (%) | 80.38 | 80.38 |
| Report Review | Pass | Pass |

EL IMAGE – FIRST REFERENCE MODULE (LINE-1)

EL IMAGE – FIRST REFERENCE MODULE (LINE-2)

- First Module Measurement

| Reference Module Serial Number | Shift | *Ref. Module/ Room Temperature (°C) | I-V Curve | EL Image Review | Fill Factor (%) | Isc (A) | Voc (V) | Imp (A) | Vmp (V) | Pmpp | Result | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| NSMS26050001569 | Day | 25.05°C | Pass | Pass | 80.55 | 15.54 | 48.60 | 41.06 | 14.81 | 608.64 | PASS | Nil |
| NSMS26050001569 | Night | 24.95°C | Pass | Pass | 80.23 | 15.57 | 48.59 | 41.07 | 14.74 | 607.31 | PASS | Nil |
| NSMG26060493685 | Night | 25.70°C | Pass | Pass | 80.38 | 15.65 | 48.55 | 41.03 | 14.86 | 610.02 | PASS | Nil |

- Calibration Verification Pictures

| Calibration Witness | Equipment Parameters (Line-1) | Equipment Parameters (Line-2) |
| --- | --- | --- |
| Front Image - 1st Reference Module (Line-1) | Rear Image - 1st Reference Module (Line-1) | Front Image - 1st Reference Module (Line-2) |
| Rear Image - 1st Reference Module (Line-2) | Room Temperature | Module Temperature (Line-1) |
| Module Temperature (Line-2) | I-V Curve First Reference Module (Line-1) | I-V Curve First Reference Module (Line-2) |

- NON-CONFORMITIES (NC) RECORD

- Non-Conformity 1

| Finding Date | 01.10.2026 | Non-Conformity Description | The cell peel test for Stringer 5 failed during the second trial on 30th September |
| --- | --- | --- | --- |
| Production Shift | A | Additional Details | / |
| Number of Affected Modules | 164 | Severity of NC | Major |
| Non-conformity Closed Immediately? | No | Manufacturing Process | Stringer |
| Immediate Action(s) by the Supplier | Status Pending | Closure Status and Follow-up Required | Yes |

| Non-Conformity Picture 1 | Non-Conformity Picture 2 |
| --- | --- |
| / | / |

- Non-Conformity 2

| Finding Date | / | Non-Conformity Description | / |
| --- | --- | --- | --- |
| Production Shift | / | Additional Details | / |
| Number of Affected Modules | / | Severity of NC | / |
| Non-conformity Closed Immediately? | / | Manufacturing Process | / |
| Immediate Action(s) by the Supplier | / | Closure Status and Follow-up Required | / |

| Non-Conformity Picture 1 | Non-Conformity Picture 2 |
| --- | --- |
| / | / |

- Non-Conformity 3

| Finding Date | / | Non-Conformity Description | / |
| --- | --- | --- | --- |
| Production Shift | / | Additional Details | / |
| Number of Affected Modules | / | Severity of NC | / |
| Non-conformity Closed Immediately? | / | Manufacturing Process | / |
| Immediate Action(s) by the Supplier | / | Closure Status and Follow-up Required | / |

| Non-Conformity Picture 1 | Non-Conformity Picture 2 |
| --- | --- |
| / | / |

- Non-Conformity 4

| Finding Date | / | Non-Conformity Description | / |
| --- | --- | --- | --- |
| Production Shift | / | Additional Details | / |
| Number of Affected Modules | / | Severity of NC | / |
| Non-conformity Closed Immediately? | / | Manufacturing Process | / |
| Immediate Action(s) by the Supplier | / | Closure Status and Follow-up Required | / |

| Non-Conformity Picture 1 | Non-Conformity Picture 2 |
| --- | --- |
| / | / |

- CUMULATIVE NON-CONFORMITIES (NC)

| Date of Finding | Description | Severity | Process | Rejected Module Sr. No. | Control type | Vendor Containment Action | Closure Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 29.09.2026 | Final EL images have some blur issues. | / | Major | Final | Auto | Stop the machine and immediately resolve the issue. | Closed |
| 30.09.2026 | Minor frame up and down was observed after framing. | Minor | Framing | / | Auto | Stop the machine and immediately resolve the issue. | Closed |
| 30.09.2026 | The cell peel test for Stringer 5 failed during the second trial. | Major | Stringer | 126 | Auto | Remove the affected modules from production and mark them as suspected modules | Closed |
| 01.10.2026 | The cell peel test for Stringer 5 failed during the second trial on 30th September | Major | Stringer | 164 | Auto | Status Pending | Open |