| Prepared By (“DSR”): | Prepared For (“Client”): |
| --- | --- |

PRE-SHIPMENT INSPECTION REPORT

For

PV Modules

| Client | : Resolven Private Ltd. |
| --- | --- |
| Project Name | : Ganeko Two Energy Private Ltd. |
| SPV Name | : Solapur Ganeko One Energy Private Ltd. - Shell - 22.9 MWp Solar |

| Report No. | : DSR-PSI-RES-2026-10-04 |
| --- | --- |
| Report Date | : 04.10.2026 |
| Manufacturer | : Premier Energies Global Environment Private Ltd. |
| Location | : SY. N:1663 TO 1673, UDL 5/Part, Seetharampur, Telangana 509217 |
| Workshop | : P7 |

TABLE OF CONTENTS

- PRE-SHIPMENT INSPECTION (PSI) SUMMARY

- General Information

- Inspection Conclusion

- Report Signatories

- INSPECTION RESULT SUMMARY

- Result Summary

- WITNESS REPORT

- Test Conditions Verification

- Client SOP for PSI

- Sun-Simulator Calibration before and during PSI

- Photographic Records

- INSPECTION ANALYSIS

- Summary of Results

- Tests Evaluation - Maximum Power Determination

- Tests Evaluation - EL Image Analysis

- Tests Evaluation - Visual Inspection

- Tests Evaluation - Dimension Check

- Tests Evaluation - Insulation Test & Ground Continuity Test

- Tests Evaluation - Wet Leakage Test

- Tests Evaluation - Bi-Faciality Test

- Tests Evaluation - Static Mechanical Load Test

- Tests Evaluation - Dynamic Mechanical Load Test

- Tests Evaluation - Robustness of Termination Test

- Tests Evaluation - Low Irradiance Test

- PRE-SHIPMENT INSPECTION (PSI) SUMMARY

- General Information

| Report Number | DSR-PSI-RES-2026-10-04 |
| --- | --- |
| Manufacturer | Premier Energies Global Environment Private Ltd. |
| Factory | P7 Hyderabad |
| Lot Number | 01 |
| Lot Size (in pcs) | 8,246 |
| Lot Size (in MWp) | 5.071 |

Output Summary based on Power Wattage

| Watt Class (Wp) | Total Modules (Nos.) | Total Wattage (MWp) | Product Type | Remarks |
| --- | --- | --- | --- | --- |
| 615 | 8,246 | 5.071 | PE-132-615THGB-G12R | N/A |
| Total | 8,246 | 5.071 | PE-132-615THGB-G12R | N/A |

- Inspection Conclusion

INSPECTION CONCLUSION

Pass

- Report Signatories

| PREPARED BY | PROJECT ENGINEER |  |
| --- | --- | --- |
| REVIEWED BY | REPORT AUDITOR |  |
| APPROVED BY | TECHNICAL MANAGER |  |

- INSPECTION RESULT SUMMARY

- Result Summary

| Inspection/Test | Testing Standard/Document Reference | AQL | Sampling | Observation | Decision | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Visual Check | As per agreed Visual Criteria-2.4 | G-1, Maj. 1.5 & Min. 2.5 | 80 | 1 | Pass | Module Replaced |
| Maximum Power Determination | 1. Average witness test Value (Wp) should be ≥ Nominal/Label Wp. 2. Individual module witness test value (Wp) shall be within ± 1% of factory measured value (Including Measurement Uncertainty). | G-1, AQL-0 | 80 | 0 | Pass | Nil |
| EL Test | As per agreed EL Criteria-2.6 | G-1, Maj. 1.5 & Min. 2.5 | 80 | 0 | Pass | Nil |
| Bi-Faciality Factor | Bi-Faciality: 80 ± 5% | 2 Nos./Lot, AQL-0 | 2 | 0 | Pass | Nil |
| Insulation Test | IEC-61215, Leakage Current shall be ＜0.02mA and IR Value shall be ≥ 1000MΩ | 5 Nos./Lot, AQL-0 | 5 | 0 | Pass | Nil |
| Wet Leakage Test | IEC-61215, IR Value shall be ≥ 1000MΩ | 5 Nos./Lot, AQL-0 | 5 | 0 | Pass | Nil |
| Ground Continuity Test | As per IEC-61730 | 5 Nos./Lot, AQL-0 | 5 | 0 | Pass | Nil |
| Dimension Inspection | As per Drawing/Datasheet approved by Resolven | 2 Nos./Lot, AQL-0 | 2 | 0 | Pass | Nil |
| Static Mechanical Load Test | As per IEC-61215 | 1 No./Lot, AQL-0 | 1 | 0 | Pass | Nil |
| Cyclic (Dynamic) Mechanical Load Test | As per IEC-61215 | 1 No./Lot, AQL-0 | 1 | 0 | Pass | Nil |
| Robustness of Terminations Test | As per IEC-61215 | 1 No./Lot, AQL-0 | 1 | 0 | Pass | Nil |
| Low Irradiance Test | As per IEC 61215-2:2016 | 1 Nos /PSI AQL-0 | 2 | 0 | Pass | 1 Extra Module Witness done for Low Irradiance. |

- WITNESS REPORT

- Test Conditions Verification

| Test | Applicable Inspection | Process | Equipment Manufacturer | Equipment Model | Equipment Sr. Number | Last Date of Calibration | Upcoming Date of Calibration | Observation | Final Evaluation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum Power Determination | Yes | Semi-Auto | GSOLAR POWER CO,,LTD | GIV-20A2616 | GS20A261626010420 | 06/07/2026 | 05/07/2027 | Nil | Pass |
| Bi-Faciality Factor | Yes | Semi-Auto | GSOLAR POWER CO,,LTD | GIV-20A2616 | GS20A261626010420 | 06/07/2026 | 05/07/2027 | Nil | Pass |
| EL Test (DC Power Supply) | Yes | Semi-Auto | Zhuhai GMEE | PS8015 | 120059 | 04/04/2026 | 03/04/2027 | Nil | Pass |
| Insulation Test (DC Power Supply) | Yes | Automatic | Hopetech | CHT9985A | CHT9985A2512020 | 23/06/2026 | 22/06/2027 | Nil | Pass |
| Wet Leakage Test (DC Power Supply) | Yes | Semi-Auto | Megger | MIT 1025/2 | PE/IT/02 | 13/05/2026 | 12/05/2027 | Nil | Pass |
| Ground Continuity Test (DC Power Supply) | Yes | Automatic | Hopetech | CHT9985A | CHT9985A2512020 | 23/06/2026 | 22/06/2027 | Nil | Pass |
| DCW Test (DC Power Supply) | Yes | Automatic | Hopetech | CHT9985A | CHT9985A2512020 | 23/06/2026 | 22/06/2027 | Nil | Pass |
| Dimension Inspection | Yes | Manual | Freemans (Measurement Tape) | IND/09/98/219 | S319-26 | 14/05/2026 | 13/05/2027 | Nil | Pass |
| Static Mechanical Load Test | Yes | Automatic | Zealwe Technology Co., Ltd. | ZW-MLTC02-02032614 | 20133196 | 26/05/2026 | 25/05/2027 | Nil | Pass |
| Cyclic (Dynamic) Mechanical Load Test | Yes | Automatic | Zealwe Technology Co., Ltd.. | ZW-MLTC02-02032614 | 20133197 | 26/05/2026 | 27/05/2027 | Nil | Pass |

- Client SOP for PSI

- Sun-Simulator Calibration before and during PSI

| Test Time | Test Performance | Sun-Simulator Equipment | Equipment Class | Equipment Serial Number | Reference Module Serial Number | EL Check | IV Check | Room Temp (°C) | Module Temp (°C) | Fill Factor (%) | Isc (A) | Voc (V) | Imp (A) | Vmp (V) | Pmpp | Result |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 03-10-2026 16:28:09 | Calibration | G solar | A+A+A+ | GS20A261626010420 | NSMS26050001569 | Pass | Pass | 24.19°C | 23.28 °C | 80.31 | 15.63 | 48.62 | 15.25 | 40.03 | 610.44 | Pass |
| 03-10-2026 17:53:54 | Validation | G solar | A+A+A+ | GS20A261626010420 | NSMS26050001569 | Pass | Pass | 24.06°C | 23.33°C | 80.31 | 15.64 | 48.64 | 15.26 | 40.03 | 610.72 | Pass |
| 03-10-2026 17:54:19 | Validation | G solar | A+A+A+ | GS20A261626010420 | NSMS26050001569 | Pass | Pass | 24.06°C | 23.34°C | 80.37 | 15.61 | 48.63 | 15.25 | 40.03 | 610.51 | Pass |
| 03-10-2026 17:54:38 | Validation | G solar | A+A+A+ | GS20A261626010420 | NSMS26050001569 | Pass | Pass | 23.93°C | 23.30°C | 80.42 | 15.61 | 48.62 | 15.24 | 40.03 | 610.40 | Pass |

INSPECTION ANALYSIS

- Summary of Results

| Test | Non-Conformity Category | Non-Conformity Description | Risk Category | No. of Non-Conformities |
| --- | --- | --- | --- | --- |
| Visual Check | Minor | Frame Scratch | Minor | 01 |
| Maximum Power Determination | N/A | N/A | N/A | N/A |
| EL Test | N/A | N/A | N/A | N/A |
| Bi-Faciality Factor | N/A | N/A | N/A | N/A |
| Insulation Test | N/A | N/A | N/A | N/A |
| Wet Leakage Test | N/A | N/A | N/A | N/A |
| Ground Continuity Test | N/A | N/A | N/A | N/A |
| Dimension Inspection | N/A | N/A | N/A | N/A |
| Static Mechanical Load Test | N/A | N/A | N/A | N/A |
| Dynamic Mechanical Load Test | N/A | N/A | N/A | N/A |
| Robustness of Terminations Test | N/A | N/A | N/A | N/A |
| Low Irradiance Test | N/A | N/A | N/A | N/A |

- Tests Evaluation - Maximum Power Determination

| Sr. No. | Module No. | Pre-PDI |  |  |  | During PDI |  |  |  | Diff. (Pmax1- Pmax) Wp | %age | Module Dimension (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Pmax | Vpm | Ipm | FF | Pmax1 | Vpm | Ipm | FF |  |  |  |
| * | NSMS26050001569 | 610.27 | 41.05 | 14.87 | 80.38 | 610.44 | 40.03 | 15.25 | 80.31 | 0.17 | 0.03% | 2382*1134*35 |
| 1 | NSME26090116872 | 622.32 | 41.11 | 15.14 | 80.84 | 620.40 | 40.25 | 15.41 | 80.12 | -1.92 | -0.31% | 2382*1134*35 |
| 2 | NSME26090116870 | 620.15 | 41.14 | 15.07 | 80.35 | 618.09 | 40.25 | 15.36 | 79.83 | -2.05 | -0.33% | 2382*1134*35 |
| 3 | NSME26090116667 | 623.66 | 41.21 | 15.13 | 80.75 | 618.17 | 40.31 | 15.34 | 79.63 | -5.48 | -0.88% | 2382*1134*35 |
| 4 | NSME26090115895 | 621.88 | 41.20 | 15.09 | 80.62 | 618.99 | 40.32 | 15.35 | 79.79 | -2.88 | -0.46% | 2382*1134*35 |
| 5 | NSME26090116769 | 622.56 | 41.21 | 15.11 | 80.88 | 619.08 | 40.28 | 15.37 | 79.87 | -3.48 | -0.56% | 2382*1134*35 |
| 6 | NSME26090116788 | 623.27 | 41.19 | 15.13 | 80.87 | 621.47 | 40.31 | 15.42 | 80.19 | -1.80 | -0.29% | 2382*1134*35 |
| 7 | NSME26090116539 | 621.98 | 41.22 | 15.09 | 80.51 | 618.95 | 40.29 | 15.36 | 79.73 | -3.03 | -0.49% | 2382*1134*35 |
| 8 | NSME26090116864 | 623.44 | 41.24 | 15.12 | 80.78 | 620.48 | 40.31 | 15.39 | 79.90 | -2.96 | -0.48% | 2382*1134*35 |
| 9 | NSME26090116811 | 619.93 | 41.23 | 15.04 | 80.38 | 620.53 | 40.30 | 15.40 | 79.74 | 0.60 | 0.10% | 2382*1134*35 |
| 10 | NSME26090116810 | 623.30 | 41.20 | 15.13 | 80.87 | 621.19 | 40.32 | 15.41 | 80.03 | -2.11 | -0.34% | 2382*1134*35 |
| 11 | NSME26090116792 | 623.27 | 41.25 | 15.11 | 80.91 | 620.99 | 40.31 | 15.40 | 80.01 | -2.28 | -0.37% | 2382*1134*35 |
| 12 | NSME26090116761 | 622.42 | 41.21 | 15.10 | 80.84 | 620.39 | 40.32 | 15.39 | 80.22 | -2.03 | -0.33% | 2382*1134*35 |
| 13 | NSME26090116249 | 624.28 | 41.19 | 15.15 | 80.90 | 620.46 | 40.31 | 15.39 | 79.90 | -3.82 | -0.61% | 2382*1134*35 |
| 14 | NSME26090116427 | 624.53 | 41.20 | 15.16 | 80.85 | 621.25 | 40.33 | 15.40 | 79.63 | -3.28 | -0.53% | 2382*1134*35 |
| 15 | NSME26090117199 | 624.02 | 41.17 | 15.16 | 80.83 | 619.56 | 40.35 | 15.36 | 79.76 | -4.46 | -0.71% | 2382*1134*35 |
| 16 | NSME26090118040 | 624.81 | 41.16 | 15.18 | 80.90 | 622.42 | 40.30 | 15.45 | 80.26 | -2.39 | -0.38% | 2382*1134*35 |
| 17 | NSME26090115834 | 623.97 | 41.17 | 15.15 | 80.95 | 621.82 | 40.33 | 15.42 | 80.30 | -2.14 | -0.34% | 2382*1134*35 |
| 18 | NSME26090115938 | 624.17 | 41.12 | 15.18 | 80.86 | 621.33 | 40.29 | 15.42 | 79.76 | -2.83 | -0.45% | 2382*1134*35 |
| 19 | NSME26090117535 | 624.40 | 41.17 | 15.17 | 80.69 | 620.14 | 40.30 | 15.39 | 80.02 | -4.26 | -0.68% | 2382*1134*35 |
| 20 | NSME26090115792 | 625.14 | 41.19 | 15.18 | 80.95 | 619.22 | 40.27 | 15.38 | 79.84 | -5.92 | -0.95% | 2382*1134*35 |
| 21 | NSME26090117786 | 625.08 | 41.24 | 15.16 | 80.90 | 620.48 | 40.29 | 15.40 | 79.94 | -4.60 | -0.74% | 2382*1134*35 |
| 22 | NSME26090118913 | 623.95 | 41.16 | 15.16 | 80.81 | 621.94 | 40.30 | 15.43 | 80.00 | -2.00 | -0.32% | 2382*1134*35 |
| 23 | NSME26090118898 | 623.67 | 41.13 | 15.16 | 80.72 | 622.27 | 40.30 | 15.44 | 80.14 | -1.41 | -0.23% | 2382*1134*35 |
| 24 | NSME26090118703 | 623.35 | 41.13 | 15.16 | 80.76 | 621.46 | 40.33 | 15.41 | 80.00 | -1.88 | -0.30% | 2382*1134*35 |
| 25 | NSME26090118684 | 623.56 | 41.11 | 15.17 | 80.77 | 619.96 | 40.31 | 15.38 | 79.86 | -3.60 | -0.58% | 2382*1134*35 |
| 26 | NSME26090118605 | 623.44 | 41.13 | 15.16 | 80.89 | 620.51 | 40.34 | 15.38 | 80.03 | -2.94 | -0.47% | 2382*1134*35 |
| 27 | NSME26090118598 | 623.65 | 41.14 | 15.16 | 80.89 | 620.60 | 40.30 | 15.40 | 79.98 | -3.05 | -0.49% | 2382*1134*35 |
| 28 | NSME26090118088 | 624.53 | 41.14 | 15.18 | 80.81 | 621.96 | 40.28 | 15.44 | 80.14 | -2.57 | -0.41% | 2382*1134*35 |
| 29 | NSME26090117847 | 624.56 | 41.20 | 15.16 | 80.94 | 622.87 | 40.32 | 15.45 | 80.05 | -1.69 | -0.27% | 2382*1134*35 |
| 30 | NSME26090118045 | 624.38 | 41.19 | 15.16 | 80.94 | 622.13 | 40.31 | 15.43 | 80.35 | -2.25 | -0.36% | 2382*1134*35 |
| 31 | NSME26090117748 | 626.05 | 41.26 | 15.17 | 80.71 | 621.99 | 40.30 | 15.43 | 79.89 | -4.06 | -0.65% | 2382*1134*35 |
| 32 | NSME26090118545 | 623.08 | 41.12 | 15.15 | 80.87 | 619.31 | 40.27 | 15.38 | 79.81 | -3.76 | -0.60% | 2382*1134*35 |
| 33 | NSME26090122598 | 622.23 | 41.24 | 15.09 | 80.84 | 620.75 | 40.29 | 15.41 | 79.99 | -1.48 | -0.24% | 2382*1134*35 |
| 34 | NSME26090123199 | 619.97 | 41.18 | 15.06 | 80.49 | 621.09 | 40.27 | 15.42 | 79.86 | 1.12 | 0.18% | 2382*1134*35 |
| 35 | NSME26090121541 | 618.20 | 41.16 | 15.02 | 80.50 | 618.27 | 40.25 | 15.36 | 79.74 | 0.08 | 0.01% | 2382*1134*35 |
| 36 | NSME26090121552 | 618.85 | 41.17 | 15.03 | 80.63 | 620.26 | 40.25 | 15.41 | 79.96 | 1.41 | 0.23% | 2382*1134*35 |
| 37 | NSME26090121525 | 620.20 | 41.21 | 15.05 | 80.55 | 620.56 | 40.32 | 15.39 | 79.93 | 0.37 | 0.06% | 2382*1134*35 |
| 38 | NSME26090122827 | 620.03 | 41.18 | 15.06 | 80.52 | 622.13 | 40.29 | 15.44 | 79.98 | 2.10 | 0.34% | 2382*1134*35 |
| 39 | NSME26090123156 | 622.01 | 41.20 | 15.10 | 80.78 | 619.63 | 40.26 | 15.39 | 79.69 | -2.38 | -0.38% | 2382*1134*35 |
| 40 | NSME26090122447 | 622.20 | 41.20 | 15.10 | 80.81 | 621.40 | 40.27 | 15.43 | 79.99 | -0.80 | -0.13% | 2382*1134*35 |
| 41 | NSME26090122730 | 619.35 | 41.18 | 15.04 | 80.27 | 622.73 | 40.30 | 15.45 | 80.02 | 3.38 | 0.55% | 2382*1134*35 |
| 42 | NSME26090123232 | 619.35 | 41.17 | 15.04 | 80.61 | 619.95 | 40.28 | 15.39 | 79.81 | 0.59 | 0.10% | 2382*1134*35 |
| 43 | NSME26090123224 | 621.74 | 41.18 | 15.10 | 81.03 | 617.23 | 40.18 | 15.36 | 79.66 | -4.50 | -0.72% | 2382*1134*35 |
| 44 | NSME26090123299 | 618.12 | 41.15 | 15.02 | 80.56 | 618.89 | 40.26 | 15.37 | 79.80 | 0.77 | 0.12% | 2382*1134*35 |
| 45 | NSME26090121888 | 615.88 | 41.14 | 14.97 | 80.16 | 619.62 | 40.32 | 15.37 | 79.77 | 3.74 | 0.61% | 2382*1134*35 |
| 46 | NSME26090121803 | 616.38 | 41.14 | 14.98 | 80.29 | 620.36 | 40.30 | 15.39 | 80.22 | 3.99 | 0.65% | 2382*1134*35 |
| 47 | NSME26090121887 | 616.17 | 41.14 | 14.98 | 80.15 | 616.03 | 40.24 | 15.31 | 79.54 | -0.14 | -0.02% | 2382*1134*35 |
| 48 | NSME26090122015 | 616.41 | 41.14 | 14.98 | 80.10 | 620.67 | 40.25 | 15.42 | 79.96 | 4.26 | 0.69% | 2382*1134*35 |
| 49 | NSME26090122061 | 617.83 | 41.18 | 15.00 | 80.41 | 617.70 | 40.27 | 15.34 | 79.63 | -0.13 | -0.02% | 2382*1134*35 |
| 50 | NSME26090121641 | 618.21 | 41.25 | 14.99 | 80.12 | 617.41 | 40.30 | 15.32 | 79.61 | -0.80 | -0.13% | 2382*1134*35 |
| 51 | NSME26090122853 | 616.37 | 41.20 | 14.96 | 80.06 | 620.58 | 40.29 | 15.40 | 79.90 | 4.22 | 0.68% | 2382*1134*35 |
| 52 | NSME26090121466 | 617.81 | 41.18 | 15.00 | 80.32 | 618.31 | 40.25 | 15.36 | 79.78 | 0.50 | 0.08% | 2382*1134*35 |
| 53 | NSME26090123071 | 618.44 | 41.22 | 15.00 | 80.24 | 618.78 | 40.32 | 15.35 | 79.85 | 0.34 | 0.05% | 2382*1134*35 |
| 54 | NSME26090123186 | 618.00 | 41.22 | 14.99 | 80.22 | 619.54 | 40.31 | 15.37 | 79.66 | 1.54 | 0.25% | 2382*1134*35 |
| 55 | NSME26090122039 | 616.21 | 41.14 | 14.98 | 80.19 | 618.95 | 40.26 | 15.37 | 79.95 | 2.74 | 0.45% | 2382*1134*35 |
| 56 | NSME26090122397 | 615.90 | 41.18 | 14.96 | 79.95 | 617.50 | 39.80 | 15.51 | 79.45 | 1.60 | 0.26% | 2382*1134*35 |
| 57 | NSME26090123237 | 622.28 | 41.21 | 15.10 | 80.96 | 621.44 | 40.28 | 15.43 | 80.21 | -0.85 | -0.14% | 2382*1134*35 |
| 58 | NSME26090123236 | 620.48 | 41.22 | 15.05 | 80.62 | 621.50 | 40.29 | 15.43 | 79.95 | 1.03 | 0.17% | 2382*1134*35 |
| 59 | NSME26090123529 | 618.41 | 41.17 | 15.02 | 80.49 | 617.22 | 40.27 | 15.33 | 79.75 | -1.19 | -0.19% | 2382*1134*35 |
| 60 | NSME26090123313 | 620.20 | 41.18 | 15.06 | 80.69 | 619.06 | 40.31 | 15.36 | 79.80 | -1.14 | -0.18% | 2382*1134*35 |
| 61 | NSME26090123463 | 619.48 | 41.17 | 15.05 | 80.66 | 615.67 | 40.26 | 15.29 | 79.11 | -3.81 | -0.62% | 2382*1134*35 |
| 62 | NSME26090122814 | 621.30 | 41.21 | 15.08 | 80.74 | 620.07 | 40.27 | 15.40 | 79.72 | -1.23 | -0.20% | 2382*1134*35 |
| 63 | NSME26090123209 | 618.91 | 41.20 | 15.02 | 80.36 | 617.09 | 40.16 | 15.36 | 79.69 | -1.82 | -0.29% | 2382*1134*35 |
| 64 | NSME26090123480 | 619.88 | 41.14 | 15.07 | 80.75 | 621.35 | 40.25 | 15.44 | 79.84 | 1.46 | 0.24% | 2382*1134*35 |
| 65 | NSME26090123287 | 618.62 | 41.18 | 15.02 | 80.52 | 621.44 | 40.36 | 15.40 | 80.28 | 2.82 | 0.46% | 2382*1134*35 |
| 66 | NSME26090123449 | 617.74 | 41.16 | 15.01 | 80.47 | 620.61 | 40.35 | 15.38 | 79.98 | 2.88 | 0.47% | 2382*1134*35 |
| 67 | NSME26090123164 | 618.57 | 41.16 | 15.03 | 80.50 | 617.29 | 40.23 | 15.34 | 79.44 | -1.28 | -0.21% | 2382*1134*35 |
| 68 | NSME26090123405 | 618.42 | 41.18 | 15.02 | 80.48 | 615.24 | 40.17 | 15.32 | 79.56 | -3.18 | -0.51% | 2382*1134*35 |
| 69 | NSME26090125833 | 620.83 | 41.26 | 15.05 | 80.83 | 622.27 | 40.32 | 15.43 | 79.91 | 1.44 | 0.23% | 2382*1134*35 |
| 70 | NSME26090125854 | 620.65 | 41.29 | 15.03 | 80.78 | 618.67 | 40.32 | 15.34 | 79.62 | -1.98 | -0.32% | 2382*1134*35 |
| 71 | NSME26090125840 | 619.57 | 41.26 | 15.01 | 80.60 | 620.16 | 40.26 | 15.40 | 80.11 | 0.59 | 0.10% | 2382*1134*35 |
| 72 | NSME26090125626 | 619.60 | 41.24 | 15.02 | 80.52 | 618.89 | 40.31 | 15.35 | 79.46 | -0.71 | -0.11% | 2382*1134*35 |
| 73 | NSME26090125872 | 619.84 | 41.23 | 15.04 | 80.70 | 617.50 | 40.29 | 15.33 | 79.68 | -2.34 | -0.38% | 2382*1134*35 |
| 74 | NSME26090125834 | 620.78 | 41.20 | 15.07 | 80.92 | 621.04 | 40.26 | 15.43 | 80.20 | 0.26 | 0.04% | 2382*1134*35 |
| 75 | NSME26090125841 | 622.55 | 41.21 | 15.11 | 80.63 | 622.40 | 40.31 | 15.44 | 79.99 | -0.15 | -0.02% | 2382*1134*35 |
| 76 | NSME26090125838 | 622.07 | 41.20 | 15.10 | 80.74 | 622.30 | 40.27 | 15.45 | 80.36 | 0.23 | 0.04% | 2382*1134*35 |
| 77 | NSME26090125842 | 621.16 | 41.22 | 15.07 | 80.56 | 620.17 | 40.30 | 15.39 | 80.04 | -0.98 | -0.16% | 2382*1134*35 |
| 78 | NSME26090125885 | 618.32 | 41.18 | 15.01 | 80.79 | 619.20 | 40.28 | 15.37 | 79.89 | 0.88 | 0.14% | 2382*1134*35 |
| 79 | NSME26090125897 | 622.04 | 41.24 | 15.08 | 80.59 | 619.83 | 40.33 | 15.37 | 79.74 | -2.21 | -0.35% | 2382*1134*35 |
| 80 | NSME26090125913 | 624.14 | 41.23 | 15.14 | 80.96 | 621.91 | 40.27 | 15.44 | 80.18 | -2.23 | -0.36% | 2382*1134*35 |
| Minimum |  | 615.88 | 41.11 | 14.96 | 79.95 | 615.24 | 39.80 | 15.29 | 79.11 | -5.92 | -0.95% | - |
| Maximum |  | 626.05 | 41.29 | 15.18 | 81.03 | 622.87 | 40.36 | 15.51 | 80.36 | 4.26 | 0.69% | - |
| Average |  | 621.06 | 41.19 | 15.08 | 80.64 | 620.01 | 40.28 | 15.39 | 79.89 | 1.03 | -0.17% | - |

- Tests Evaluation - EL Image Analysis

- Non-Conforming Modules Summary

| Defect Description | Acceptance Limit |  | Observed |  | Evaluation |
| --- | --- | --- | --- | --- | --- |
|  | Major (1.5) | Minor (2.5) | Major | Minor |  |
| N/A | 03 | 05 | 0 | 0 | Pass |

- Non-Conforming Modules

| Sr. No. | Module Serial No. | Defect Representation | Picture |
| --- | --- | --- | --- |
| 1 | N/A | N/A | N/A |
| 2 | N/A | N/A | N/A |

- EL Pictures of 81 Modules (including Golden Module):

- Tests Evaluation - Visual Inspection

- Non-Conforming Modules Summary

| Defect Description | Acceptance Limit |  | Observed |  | Evaluation |
| --- | --- | --- | --- | --- | --- |
|  | Major (1.5) | Minor (2.5) | Major | Minor |  |
| - Frame Scratch - 1No | 03 | 05 | 00 | 01 | Pass |

- Non-Conforming Modules

| Sr. No. | Module Serial No. | Defect Representation | Picture |
| --- | --- | --- | --- |
| 1. | NSME26090115792 | Frame Scratch |  |

- Tests Evaluation - Dimension Check

- Non-Conforming Modules Summary

| Defect Description | Acceptance Limit |  | Observed |  | Evaluation |
| --- | --- | --- | --- | --- | --- |
|  | Major (1.5) | Minor (2.5) | Major (1.5) | Minor (2.5) |  |
| N/A | 0 | 0 | 0 | 0 | Pass |

- Non-Conforming Modules

| Sr. No. | Module Serial No. | Defect Representation | Picture |
| --- | --- | --- | --- |
| N/A | N/A | N/A | N/A |
| N/A | N/A | N/A | N/A |

- Photographic Records

| Front Side Picture | Back Side Picture | Label Picture (615W) |
| --- | --- | --- |
| Pallet Picture | Pallet Picture | Packing List Picture |
| Hipot Test Equipment Picture | I-V Test Equipment Picture | EL Test Equipment Picture |
| DCW, IR, GD Test | Wet Leakage Test | Length (mm) |

| Width (mm) | Diagonal (mm) | Distance Between Mounting Holes-Width Side (mm) |
| --- | --- | --- |
| Distance Between Mounting Holes-1 (mm) | Distance Between Mounting Holes-2 (mm) | Distance Between Mounting Holes-3 (mm) |
| Positive Cable Length (mm) | Negative Cable Length (mm) | Frame Height Dimension (mm) |
| Frame Width Dimension (mm) | Anodizing Thickness (μm) | Frame Wall Thickness Dimension (mm) |
| Label Picture (615W) – High Resolution |  |  |

- Tests Evaluation - Insulation Test & Ground Continuity Test

- Test Report

| Sr. No. | Module No. | DCW: 8 kV, <20 μA | IR: 1.5 kV, ≥1000 MΩ. | GND: 75A, <0.1 Ohm | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1. | NSME26090123156 | 1.1 µA | 18010 MΩ | 1.844 mΩ | Pass |
| 2. | NSME26090123480 | 1.7 µA | 27740 MΩ | 2.658 mΩ | Pass |
| 3. | NSME26090116761 | 1.2 µA | 16220 MΩ | 7.240 mΩ | Pass |
| 4. | NSME26090115938 | 1.7 µA | 15890 MΩ | 4.941 mΩ | Pass |
| 5. | NSME26090122039 | 1.2 µA | 20850 MΩ | 4.387 mΩ | Pass |

- Photographic Records

| Sample-1 | Sample-2 | Sample-3 |
| --- | --- | --- |
| Sample-4 | Sample-5 | Machine Photo |

- Tests Evaluation - Wet Leakage Test

- Test Report

| Sr. No. | Module ID | Module Type | Applied Voltage (V) | Test Time (Sec.) | Result (≥1000MΩ) | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | NSME26090115792 | PE-132-615THGB-G12R | 1500 V | 120 Sec. | 13860 MΩ | Pass |
| 2. | NSME26090121466 | PE-132-615THGB-G12R | 1500 V | 120 Sec. | 9780 MΩ | Pass |
| 3. | NSME26090125897 | PE-132-615THGB-G12R | 1500 V | 120 Sec. | 14300 MΩ | Pass |
| 4. | NSME26090117748 | PE-132-615THGB-G12R | 1500 V | 120 Sec. | 11510 MΩ | Pass |
| 5. | NSME26090123287 | PE-132-615THGB-G12R | 1500 V | 120 Sec. | 8470 MΩ | Pass |

- Photographic Records

| Sample-1 | Sample-2 | Sample-3 |
| --- | --- | --- |
| Sample-4 | Sample-5 | Wet Leakage Photo |

- Tests Evaluation - Bi-Faciality Factor

- Test Report

| Sr. No. | Module No. | Module Type | Front Side Electrical Data |  |  |  | Back Side Electrical Data |  |  |  | Pmax (80±5%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Pmax | Vpm | Ipm | FF (%) | Pmax | Vpm | Ipm | FF (%) |  |
| 1. | NSME26090118545 | PE-132-615THGB-G12R | 619.31 | 40.27 | 15.38 | 79.81 | 480.19 | 41.10 | 11.68 | 79.46 | 77.54% |
| 2. | NSME26090122397 | PE-132-615THGB-G12R | 617.50 | 39.80 | 15.51 | 79.45 | 479.53 | 41.11 | 11.66 | 79.50 | 77.67% |

- Tests Evaluation - Dynamic Mechanical Load Test

- Test Report

| Sr. No. | Module ID | Before Test (Visual) | After Test (Visual) | Before Test (Pmax) | After Test (Pmax) | Degradation (%) | Wet Leakage (≥1000MΩ) | Result |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. | NSME26090115889 | Found Ok | Found Ok | 621.19 | 617.51 | -0.59% | 10.12 GΩ | Pass |

- Photographic Records

| Dynamic Mechanical Load Test Set Up | Wet Leakage | DMLT Test Parameters |
| --- | --- | --- |

- Tests Evaluation - Static Mechanical Load Test

- Test Report

| Sr. No. | Module ID | Before Test (Visual) | After Test (Visual) | Before Test (Pmax) | After Test (Pmax) | Degradation (%) | Wet Leakage (≥1000MΩ) | Result |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. | NSME26090115975 | Found Ok | Found Ok | 619.08 | 618.44 | -0.10% | 7.83 GΩ | Pass |

- Photographic Records

| Static Mechanical Load Test Set Up | Wet Leakage | SMLT Test Parameters |
| --- | --- | --- |

- Tests Evaluation - Robustness of Termination Test

- Test Report

| Sr. No. | Module ID | Before Test (Visual) | After Test (Visual) | Before Test (Pmax) | After Test (Pmax) | Degradation (%) | Wet Leakage (≥1000MΩ) | Result |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. | NSME26090125885 | Found Ok | Found Ok | 619.20 | 616.66 | -0.41% | 12.37 GΩ | Pass |

- Photographic Records

| Robustness Test | Module Serial No. | Wet Leakage Result |
| --- | --- | --- |

- Tests Evaluation - Low Irradiance Test

- Test Report

| Sr. No. | Module No. | Module Type | 1000 W/m² (Pmax) |  |  |  | 200 W/m² (Pmax1) |  |  |  | (Pmax1/Pmax)*5 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Pmax | Vpm | Ipm | FF (%) | Pmax1 | Vpm | Ipm | FF (%) |  |
| 1. | NSME26090123405 | PE-132-615THGB-G12R | 615.24 | 40.17 | 15.31 | 79.56 | 122.45 | 40.17 | 3.04 | 83.23 | 99.51% |
| 2. | NSME26090123209 | PE-132-615THGB-G12R | 617.09 | 40.16 | 15.36 | 79.69 | 122.93 | 40.15 | 3.06 | 83.43 | 99.61% |