| Prepared By (“DSR”): | Prepared For (“Client”): |
| --- | --- |

PRE-SHIPMENT INSPECTION REPORT

For

PV Modules

| Client | : Resolven Private Ltd. |
| --- | --- |
| Project Name | : Ganeko Two Energy Private Ltd. |
| SPV Name | : Solapur Ganeko One Energy Private Ltd. - Shell - 22.9 MWp Solar |

| Report No. | : DSR-PSI-RES-2026-10-07 |
| --- | --- |
| Report Date | : 07.10.2026 |
| Manufacturer | : Premier Energies Global Environment Private Ltd. |
| Location | : SY. N:1663 TO 1673, UDL 5/Part, Seetharampur, Telangana 509217 |
| Workshop | : P7 |

TABLE OF CONTENTS

- PRE-SHIPMENT INSPECTION (PSI) SUMMARY

- General Information

- Inspection Conclusion

- Report Signatories

- INSPECTION RESULT SUMMARY

- Result Summary

- WITNESS REPORT

- Test Conditions Verification

- Client SOP for PSI

- Sun-Simulator Calibration before and during PSI

- INSPECTION ANALYSIS

- Summary of Results

- Tests Evaluation - Maximum Power Determination

- Tests Evaluation - EL Image Analysis

- Tests Evaluation - Visual Inspection

- Tests Evaluation - Dimension Check

- Tests Evaluation - Insulation Test & Ground Continuity Test

- Tests Evaluation - Wet Leakage Test

- Tests Evaluation - Bi-Faciality Test

- Tests Evaluation - Static Mechanical Load Test

- Tests Evaluation - Dynamic Mechanical Load Test

- Tests Evaluation - Robustness of Termination Test

- Tests Evaluation - Low Irradiance Test

- PRE-SHIPMENT INSPECTION (PSI) SUMMARY

- General Information

| Report Number | DSR-PSI-RES-2026-10-07 |
| --- | --- |
| Manufacturer | Premier Energies Global Environment Private Ltd. |
| Factory | P7 Hyderabad |
| Lot Number | 02 |
| Lot Size (in pcs) | 6,820 |
| Lot Size (in MWp) | 4.1943 |

Output Summary based on Power Wattage

| Watt Class (Wp) | Total Modules (Nos.) | Total Wattage (MWp) | Product Type | Remarks |
| --- | --- | --- | --- | --- |
| 615 | 6,820 | 4.1943 | PE-132-615THGB-G12R | N/A |
| Total | 6,820 | 4.1943 | PE-132-615THGB-G12R | N/A |

- Inspection Conclusion

INSPECTION CONCLUSION

Pass

- Report Signatories

| PREPARED BY | PROJECT ENGINEER |  |
| --- | --- | --- |
| REVIEWED BY | REPORT AUDITOR |  |
| APPROVED BY | TECHNICAL MANAGER |  |

- INSPECTION RESULT SUMMARY

- Result Summary

| Inspection/Test | Testing Standard/Document Reference | AQL | Sampling | Observation | Decision | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Visual Check | As per agreed Visual Criteria-2.4 | G-1, Maj. 1.5 & Min. 2.5 | 80 | 1 | Pass | Module Replaced |
| Maximum Power Determination | 1. Average witness test Value (Wp) should be ≥ Nominal/Label Wp. 2. Individual module witness test value (Wp) shall be within ± 1% of factory measured value (Including Measurement Uncertainty). | G-1, AQL-0 | 80 | 0 | Pass | Nil |
| EL Test | As per agreed EL Criteria-2.6 | G-1, Maj. 1.5 & Min. 2.5 | 80 | 0 | Pass | Nil |
| Bi-Faciality Factor | Bi-Faciality: 80 ± 5% | 2 Nos./Lot, AQL-0 | 2 | 0 | Pass | Nil |
| Insulation Test | IEC-61215, Leakage Current shall be ＜0.02mA and IR Value shall be ≥ 1000MΩ | 5 Nos./Lot, AQL-0 | 5 | 0 | Pass | Nil |
| Wet Leakage Test | IEC-61215, IR Value shall be ≥ 1000MΩ | 5 Nos./Lot, AQL-0 | 5 | 0 | Pass | Nil |
| Ground Continuity Test | As per IEC-61730 | 5 Nos./Lot, AQL-0 | 5 | 0 | Pass | Nil |
| Dimension Inspection | As per Drawing/Datasheet approved by Resolven | 2 Nos./Lot, AQL-0 | 2 | 0 | Pass | Nil |
| Static Mechanical Load Test | As per IEC-61215 | 1 No./Lot, AQL-0 | 0 | 0 | Pass | Nil |
| Cyclic (Dynamic) Mechanical Load Test | As per IEC-61215 | 1 No./Lot, AQL-0 | 0 | 0 | Pass | Nil |
| Robustness of Terminations Test | As per IEC-61215 | 1 No./Lot, AQL-0 | 1 | 0 | Pass | Nil |
| Low Irradiance Test | As per IEC 61215-2:2016 | 1 Nos /PSI AQL-0 | 1 | 0 | Pass | Nil |

Note: No SMLT or DMLT testing was performed on this lot after approval. 10 modules from this PSI are being held for third-party laboratory testing.

- WITNESS REPORT

- Test Conditions Verification

| Test | Applicable Inspection | Process | Equipment Manufacturer | Equipment Model | Equipment Sr. Number | Last Date of Calibration | Upcoming Date of Calibration | Observation | Final Evaluation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Maximum Power Determination | Yes | Semi-Auto | GSOLAR POWER CO,LTD | GIV-20A2616 | GS20A261626010420 | 06/07/2026 | 05/07/2027 | Nil | Pass |
| Bi-Faciality Factor | Yes | Semi-Auto | GSOLAR POWER CO,LTD | GIV-20A2616 | GS20A261626010420 | 06/07/2026 | 05/07/2027 | Nil | Pass |
| EL Test (DC Power Supply) | Yes | Semi-Auto | Zhuhai GMEE | PS8015 | 120059 | 04/04/2026 | 03/04/2027 | Nil | Pass |
| Insulation Test (DC Power Supply) | Yes | Automatic | Hopetech | CHT9985A | CHT9985A2512020 | 23/06/2026 | 22/06/2027 | Nil | Pass |
| Wet Leakage Test (DC Power Supply) | Yes | Semi-Auto | Megger | MIT 1025/2 | PE/IT/02 | 13/05/2026 | 12/05/2027 | Nil | Pass |
| Ground Continuity Test (DC Power Supply) | Yes | Automatic | Hopetech | CHT9985A | CHT9985A2512020 | 23/06/2026 | 22/06/2027 | Nil | Pass |
| DCW Test (DC Power Supply) | Yes | Automatic | Hopetech | CHT9985A | CHT9985A2512020 | 23/06/2026 | 22/06/2027 | Nil | Pass |
| Dimension Inspection | Yes | Manual | Freemans (Measurement Tape) | IND/09/98/219 | S319-26 | 14/05/2026 | 13/05/2027 | Nil | Pass |

- Client SOP for PSI

- Sun-Simulator Calibration before and during PSI

| Test Time | Test Performance | Sun-Simulator Equipment | Equipment Class | Equipment Serial Number | Reference Module Serial Number | EL Check | IV Check | Room Temp (°C) | Module Temp (°C) | Fill Factor (%) | Isc (A) | Voc (V) | Imp (A) | Vmp (V) | Pmpp | Result |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 05-10-2026 17:26:07 | Calibration | G solar | A+A+A+ | GS20A261626010420 | NSMS26050001569 | Pass | Pass | 25.00 | 24.50 | 80.35 | 15.62 | 48.62 | 15.21 | 40.12 | 610.28 | Pass |
|  | Calibration- 1 |  |  |  |  |  |  | 24.88 | 23.83 | 80.32 | 15.62 | 48.62 | 15.21 | 40.13 | 610.13 | Pass |
|  | Calibration- 2 |  |  |  |  |  |  | 24.81 | 23.85 | 80.36 | 15.62 | 48.62 | 15.20 | 40.14 | 610.17 | Pass |
|  | Calibration- 3 |  |  |  |  |  |  | 24.81 | 23.86 | 80.38 | 15.61 | 48.62 | 15.20 | 40.13 | 610.17 | Pass |
| 05-10-2026 19:00:52 | Validation | G solar | A+A+A+ | GS20A261626010420 | NSMS26050001569 | Pass | Pass | 24.31 | 23.70 | 80.45 | 15.61 | 48.60 | 15.22 | 40.09 | 610.34 | Pass |
|  |  |  |  |  |  |  |  | 24.31 | 23.71 | 80.44 | 15.60 | 48.60 | 15.22 | 40.09 | 610.22 | Pass |
|  |  |  |  |  |  |  |  | 24.25 | 23.66 | 80.46 | 15.60 | 48.60 | 15.23 | 40.08 | 610.28 | Pass |

- INSPECTION ANALYSIS

- Summary of Results

| Test | Non-Conformity Category | Non-Conformity Description | Risk Category | No. of Non-Conformities |
| --- | --- | --- | --- | --- |
| Visual Check | Major | Air Bubble (Terminal bubble) | Major | 01 |
| Maximum Power Determination | N/A | N/A | N/A | N/A |
| EL Test | N/A | N/A | N/A | N/A |
| Bi-Faciality Factor | N/A | N/A | N/A | N/A |
| Insulation Test | N/A | N/A | N/A | N/A |
| Wet Leakage Test | N/A | N/A | N/A | N/A |
| Ground Continuity Test | N/A | N/A | N/A | N/A |
| Dimension Inspection | N/A | N/A | N/A | N/A |
| Static Mechanical Load Test | N/A | N/A | N/A | N/A |
| Dynamic Mechanical Load Test | N/A | N/A | N/A | N/A |
| Robustness of Terminations Test | N/A | N/A | N/A | N/A |
| Low Irradiance Test | N/A | N/A | N/A | N/A |

- Tests Evaluation - Maximum Power Determination

| Sr. No. | Module No. | Pre-PDI |  |  |  | During PDI |  |  |  | Diff. (Pmax1- Pmax) Wp | %age | Module Dimension (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Pmax | Vpm | Ipm | FF | Pmax1 | Vpm | Ipm | FF |  |  |  |
| * | NSMS26050001569 | 610.27 | 41.05 | 14.87 | 80.38 | 610.13 | 40.13 | 15.21 | 80.32 | -0.14 | -0.02% | 2382*1134*35 |
| 1 | NSME26090124462 | 618.99 | 41.28 | 15.00 | 80.47 | 622.53 | 40.26 | 15.46 | 79.93 | 3.54 | 0.57% | 2382*1134*35 |
| 2 | NSME26090127548 | 619.04 | 41.27 | 15.00 | 80.49 | 619.84 | 40.26 | 15.40 | 79.63 | 0.80 | 0.13% | 2382*1134*35 |
| 3 | NSME26090127449 | 616.81 | 41.25 | 14.95 | 80.27 | 619.34 | 40.26 | 15.38 | 79.93 | 2.52 | 0.41% | 2382*1134*35 |
| 4 | NSME26090127525 | 615.81 | 41.16 | 14.96 | 80.20 | 621.44 | 40.23 | 15.45 | 79.89 | 5.63 | 0.91% | 2382*1134*35 |
| 5 | NSME26090127286 | 618.55 | 41.24 | 15.00 | 80.51 | 620.50 | 40.28 | 15.41 | 79.74 | 1.95 | 0.32% | 2382*1134*35 |
| 6 | NSME26090126622 | 618.27 | 41.32 | 14.96 | 80.31 | 622.62 | 40.29 | 15.45 | 80.12 | 4.35 | 0.70% | 2382*1134*35 |
| 7 | NSME26090126240 | 617.94 | 41.24 | 14.98 | 80.33 | 620.63 | 40.24 | 15.42 | 79.97 | 2.69 | 0.44% | 2382*1134*35 |
| 8 | NSME26090127426 | 616.19 | 41.21 | 14.95 | 80.26 | 620.81 | 40.19 | 15.45 | 79.87 | 4.63 | 0.75% | 2382*1134*35 |
| 9 | NSME26090127554 | 615.65 | 41.25 | 14.92 | 80.10 | 621.51 | 40.19 | 15.46 | 79.99 | 5.87 | 0.95% | 2382*1134*35 |
| 10 | NSME26090127594 | 616.37 | 41.20 | 14.96 | 80.27 | 619.34 | 40.23 | 15.39 | 79.68 | 2.97 | 0.48% | 2382*1134*35 |
| 11 | NSME26090127632 | 619.47 | 41.30 | 15.00 | 80.38 | 620.76 | 40.21 | 15.44 | 79.79 | 1.29 | 0.21% | 2382*1134*35 |
| 12 | NSME26090127518 | 615.82 | 41.17 | 14.96 | 80.27 | 621.49 | 40.20 | 15.46 | 80.07 | 5.67 | 0.92% | 2382*1134*35 |
| 13 | NSME26090125763 | 619.31 | 41.24 | 15.02 | 80.41 | 618.92 | 40.20 | 15.40 | 79.94 | -0.40 | -0.06% | 2382*1134*35 |
| 14 | NSME26090125747 | 619.82 | 41.22 | 15.04 | 80.50 | 619.34 | 40.22 | 15.40 | 80.04 | -0.48 | -0.08% | 2382*1134*35 |
| 15 | NSME26090125853 | 622.50 | 41.24 | 15.10 | 80.83 | 619.25 | 40.26 | 15.38 | 79.99 | -3.25 | -0.52% | 2382*1134*35 |
| 16 | NSME26090125830 | 622.76 | 41.23 | 15.11 | 80.84 | 619.88 | 40.20 | 15.42 | 79.67 | -2.88 | -0.46% | 2382*1134*35 |
| 17 | NSME26090125843 | 621.14 | 41.24 | 15.06 | 80.50 | 619.55 | 40.24 | 15.40 | 79.48 | -1.59 | -0.26% | 2382*1134*35 |
| 18 | NSME26090125882 | 623.14 | 41.22 | 15.12 | 80.76 | 617.34 | 40.22 | 15.35 | 79.99 | -5.79 | -0.93% | 2382*1134*35 |
| 19 | NSME26090125875 | 620.31 | 41.19 | 15.06 | 80.89 | 620.23 | 40.18 | 15.44 | 79.98 | -0.09 | -0.01% | 2382*1134*35 |
| 20 | NSME26090125919 | 621.31 | 41.23 | 15.07 | 80.92 | 620.16 | 40.19 | 15.43 | 79.75 | -1.15 | -0.18% | 2382*1134*35 |
| 21 | NSME26090125958 | 620.04 | 41.25 | 15.03 | 80.73 | 619.43 | 40.19 | 15.41 | 79.59 | -0.61 | -0.10% | 2382*1134*35 |
| 22 | NSME26090125955 | 620.20 | 41.24 | 15.04 | 81.03 | 619.82 | 40.22 | 15.41 | 80.05 | -0.38 | -0.06% | 2382*1134*35 |
| 23 | NSME26090125973 | 621.17 | 41.29 | 15.04 | 80.85 | 618.03 | 40.23 | 15.36 | 79.54 | -3.14 | -0.51% | 2382*1134*35 |
| 24 | NSME26090125942 | 621.54 | 41.32 | 15.04 | 81.01 | 620.42 | 40.21 | 15.43 | 79.92 | -1.12 | -0.18% | 2382*1134*35 |
| 25 | NSME26090117105 | 624.03 | 41.21 | 15.14 | 80.72 | 620.99 | 40.21 | 15.44 | 79.89 | -3.03 | -0.49% | 2382*1134*35 |
| 26 | NSME26090116366 | 622.56 | 41.23 | 15.10 | 80.69 | 620.84 | 40.23 | 15.43 | 79.97 | -1.72 | -0.28% | 2382*1134*35 |
| 27 | NSME26090117073 | 623.73 | 41.25 | 15.12 | 80.77 | 621.13 | 40.19 | 15.45 | 79.80 | -2.60 | -0.42% | 2382*1134*35 |
| 28 | NSME26090116804 | 621.82 | 41.23 | 15.08 | 80.83 | 617.83 | 40.19 | 15.37 | 79.95 | -3.99 | -0.64% | 2382*1134*35 |
| 29 | NSME26090117148 | 623.17 | 41.25 | 15.11 | 80.85 | 619.30 | 40.25 | 15.39 | 79.99 | -3.86 | -0.62% | 2382*1134*35 |
| 30 | NSME26090117176 | 623.73 | 41.23 | 15.13 | 80.72 | 620.98 | 40.22 | 15.44 | 80.10 | -2.75 | -0.44% | 2382*1134*35 |
| 31 | NSME26090117166 | 623.28 | 41.26 | 15.10 | 80.77 | 620.63 | 40.25 | 15.42 | 79.94 | -2.64 | -0.42% | 2382*1134*35 |
| 32 | NSME26090117149 | 622.74 | 41.23 | 15.11 | 80.81 | 620.10 | 40.21 | 15.42 | 80.02 | -2.64 | -0.42% | 2382*1134*35 |
| 33 | NSME26090116992 | 623.52 | 41.20 | 15.13 | 80.77 | 620.28 | 40.21 | 15.43 | 79.78 | -3.24 | -0.52% | 2382*1134*35 |
| 34 | NSME26090117185 | 620.83 | 41.23 | 15.06 | 80.38 | 619.70 | 40.24 | 15.40 | 79.67 | -1.13 | -0.18% | 2382*1134*35 |
| 35 | NSME26090117217 | 620.57 | 41.20 | 15.06 | 80.26 | 619.07 | 40.22 | 15.39 | 79.83 | -1.50 | -0.24% | 2382*1134*35 |
| 36 | NSME26090117194 | 622.96 | 41.22 | 15.11 | 80.72 | 620.43 | 40.23 | 15.42 | 79.99 | -2.52 | -0.40% | 2382*1134*35 |
| 37 | NSME26100029513 | 624.43 | 41.24 | 15.14 | 80.74 | 622.11 | 40.26 | 15.45 | 80.05 | -2.32 | -0.37% | 2382*1134*35 |
| 38 | NSME26100029325 | 621.41 | 41.17 | 15.09 | 80.54 | 621.45 | 40.34 | 15.41 | 79.99 | 0.03 | 0.01% | 2382*1134*35 |
| 39 | NSME26100029695 | 622.63 | 41.16 | 15.13 | 80.66 | 620.22 | 40.31 | 15.39 | 79.77 | -2.41 | -0.39% | 2382*1134*35 |
| 40 | NSME26100029639 | 621.03 | 41.20 | 15.07 | 80.47 | 620.96 | 40.36 | 15.38 | 79.85 | -0.06 | -0.01% | 2382*1134*35 |
| 41 | NSME26100029735 | 622.92 | 41.13 | 15.15 | 80.59 | 622.27 | 40.26 | 15.46 | 80.08 | -0.65 | -0.10% | 2382*1134*35 |
| 42 | NSME26100029457 | 622.25 | 41.24 | 15.09 | 80.71 | 621.54 | 40.31 | 15.42 | 80.08 | -0.71 | -0.11% | 2382*1134*35 |
| 43 | NSME26100003223 | 622.74 | 41.16 | 15.13 | 80.55 | 620.27 | 40.22 | 15.42 | 79.62 | -2.46 | -0.40% | 2382*1134*35 |
| 44 | NSME26100029558 | 621.18 | 41.17 | 15.09 | 80.48 | 620.42 | 40.26 | 15.41 | 79.66 | -0.76 | -0.12% | 2382*1134*35 |
| 45 | NSME26100029770 | 620.53 | 41.12 | 15.09 | 80.54 | 620.07 | 40.24 | 15.41 | 79.72 | -0.45 | -0.07% | 2382*1134*35 |
| 46 | NSME26100029766 | 620.24 | 41.12 | 15.08 | 80.35 | 619.96 | 40.25 | 15.40 | 79.66 | -0.28 | -0.05% | 2382*1134*35 |
| 47 | NSME26100029708 | 620.68 | 41.15 | 15.08 | 80.28 | 620.79 | 40.27 | 15.42 | 79.82 | 0.12 | 0.02% | 2382*1134*35 |
| 48 | NSME26100029707 | 621.25 | 41.15 | 15.10 | 80.45 | 620.18 | 40.29 | 15.39 | 79.48 | -1.07 | -0.17% | 2382*1134*35 |
| 49 | NSME26090124207 | 618.46 | 41.29 | 14.98 | 80.46 | 619.94 | 40.25 | 15.40 | 79.96 | 1.48 | 0.24% | 2382*1134*35 |
| 50 | NSME26090117344 | 619.85 | 41.52 | 14.93 | 80.59 | 619.03 | 40.24 | 15.38 | 79.87 | -0.83 | -0.13% | 2382*1134*35 |
| 51 | NSME26090116263 | 620.93 | 41.49 | 14.96 | 80.80 | 619.12 | 40.21 | 15.40 | 79.79 | -1.82 | -0.29% | 2382*1134*35 |
| 52 | NSME26090116839 | 622.05 | 41.48 | 14.99 | 80.88 | 618.98 | 40.20 | 15.40 | 79.81 | -3.07 | -0.49% | 2382*1134*35 |
| 53 | NSME26090123845 | 620.06 | 41.33 | 15.00 | 80.41 | 617.16 | 40.25 | 15.33 | 79.13 | -2.91 | -0.47% | 2382*1134*35 |
| 54 | NSME26090123615 | 618.02 | 41.25 | 14.98 | 80.50 | 619.31 | 40.20 | 15.41 | 79.70 | 1.29 | 0.21% | 2382*1134*35 |
| 55 | NSME26090123496 | 618.32 | 41.29 | 14.98 | 80.31 | 616.30 | 40.22 | 15.32 | 79.06 | -2.03 | -0.33% | 2382*1134*35 |
| 56 | NSME26090122895 | 618.35 | 41.24 | 14.99 | 80.30 | 618.91 | 40.18 | 15.41 | 79.62 | 0.56 | 0.09% | 2382*1134*35 |
| 57 | NSME26090125166 | 618.61 | 41.27 | 14.99 | 80.42 | 617.92 | 40.26 | 15.35 | 79.60 | -0.68 | -0.11% | 2382*1134*35 |
| 58 | NSME26090123610 | 617.97 | 41.25 | 14.98 | 80.43 | 620.35 | 40.23 | 15.42 | 79.90 | 2.38 | 0.39% | 2382*1134*35 |
| 59 | NSME26090123940 | 619.83 | 41.31 | 15.00 | 80.43 | 616.80 | 40.24 | 15.33 | 79.22 | -3.02 | -0.49% | 2382*1134*35 |
| 60 | NSME26090124403 | 618.48 | 41.30 | 14.98 | 80.22 | 621.58 | 40.26 | 15.44 | 79.88 | 3.10 | 0.50% | 2382*1134*35 |
| 61 | NSME26100028671 | 622.42 | 41.62 | 14.95 | 80.64 | 618.53 | 40.34 | 15.33 | 79.38 | -3.89 | -0.63% | 2382*1134*35 |
| 62 | NSME26100028666 | 621.43 | 41.63 | 14.93 | 80.76 | 620.13 | 40.33 | 15.38 | 80.04 | -1.30 | -0.21% | 2382*1134*35 |
| 63 | NSME26100028664 | 621.35 | 41.56 | 14.95 | 80.61 | 620.78 | 40.33 | 15.39 | 79.96 | -0.56 | -0.09% | 2382*1134*35 |
| 64 | NSME26100028682 | 622.88 | 41.62 | 14.97 | 80.74 | 621.35 | 40.29 | 15.42 | 79.99 | -1.53 | -0.25% | 2382*1134*35 |
| 65 | NSME26100028661 | 616.32 | 41.14 | 14.98 | 80.06 | 619.66 | 40.29 | 15.38 | 79.91 | 3.34 | 0.54% | 2382*1134*35 |
| 66 | NSME26100003753 | 622.86 | 41.67 | 14.95 | 80.94 | 620.63 | 40.31 | 15.40 | 80.03 | -2.24 | -0.36% | 2382*1134*35 |
| 67 | NSME26100001762 | 619.83 | 41.59 | 14.90 | 80.47 | 618.64 | 40.36 | 15.33 | 79.84 | -1.19 | -0.19% | 2382*1134*35 |
| 68 | NSME26100001852 | 622.62 | 41.67 | 14.94 | 80.62 | 620.55 | 40.19 | 15.44 | 79.85 | -2.07 | -0.33% | 2382*1134*35 |
| 69 | NSME26100003188 | 622.72 | 41.54 | 14.99 | 80.70 | 622.50 | 40.29 | 15.45 | 80.09 | -0.22 | -0.03% | 2382*1134*35 |
| 70 | NSME26100000795 | 623.34 | 41.55 | 15.00 | 80.80 | 622.13 | 40.29 | 15.44 | 80.11 | -1.21 | -0.19% | 2382*1134*35 |
| 71 | NSME26100000648 | 623.46 | 41.61 | 14.98 | 80.55 | 619.53 | 40.30 | 15.37 | 79.58 | -3.93 | -0.63% | 2382*1134*35 |
| 72 | NSME26100000641 | 621.40 | 41.53 | 14.96 | 80.80 | 620.93 | 40.19 | 15.45 | 80.11 | -0.47 | -0.07% | 2382*1134*35 |
| 73 | NSME26100002956 | 620.36 | 41.27 | 15.03 | 80.59 | 622.15 | 40.31 | 15.44 | 79.74 | 1.79 | 0.29% | 2382*1134*35 |
| 74 | NSME26100002994 | 619.82 | 41.21 | 15.04 | 80.45 | 621.22 | 40.26 | 15.43 | 79.74 | 1.40 | 0.23% | 2382*1134*35 |
| 75 | NSME26100002995 | 619.31 | 41.20 | 15.03 | 80.74 | 619.83 | 40.23 | 15.41 | 79.69 | 0.52 | 0.08% | 2382*1134*35 |
| 76 | NSME26100002991 | 620.00 | 41.22 | 15.04 | 80.80 | 621.80 | 40.27 | 15.44 | 80.00 | 1.80 | 0.29% | 2382*1134*35 |
| 77 | NSME26100003024 | 620.88 | 41.30 | 15.03 | 80.84 | 619.38 | 40.27 | 15.38 | 79.72 | -1.50 | -0.24% | 2382*1134*35 |
| 78 | NSME26100002998 | 622.08 | 41.35 | 15.04 | 80.63 | 621.58 | 40.28 | 15.43 | 79.92 | -0.50 | -0.08% | 2382*1134*35 |
| 79 | NSME26100002987 | 620.57 | 41.28 | 15.03 | 80.66 | 618.80 | 40.26 | 15.37 | 79.44 | -1.77 | -0.29% | 2382*1134*35 |
| 80 | NSME26100002976 | 619.05 | 41.22 | 15.02 | 80.75 | 619.87 | 40.24 | 15.40 | 79.76 | 0.82 | 0.13% | 2382*1134*35 |
| Maximum |  | 624.43 | 41.67 | 15.15 | 81.03 | 622.62 | 40.36 | 15.46 | 80.12 | 5.87 | 0.95 | - |
| Minimum |  | 615.65 | 41.12 | 14.90 | 80.06 | 616.30 | 40.18 | 15.32 | 79.06 | -5.79 | -0.93 | - |
| Average |  | 620.63 | 41.29 | 15.03 | 80.58 | 620.13 | 40.25 | 15.41 | 79.82 | -0.50 | -0.08 | - |

- Tests Evaluation - EL Image Analysis

- Non-Conforming Modules Summary

| Defect Description | Acceptance Limit |  | Observed |  | Evaluation |
| --- | --- | --- | --- | --- | --- |
|  | Major (1.5) | Minor (2.5) | Major | Minor |  |
| N/A | 03 | 05 | 0 | 0 | Pass |

- Non-Conforming Modules

| Sr. No. | Module Serial No. | Defect Representation | Picture |
| --- | --- | --- | --- |
| N/A | N/A | N/A | N/A |

- EL Pictures of 81 Modules (including Golden Module):

- Tests Evaluation - Visual Inspection

- Non-Conforming Modules Summary

| Defect Description | Acceptance Limit |  | Observed |  | Evaluation |
| --- | --- | --- | --- | --- | --- |
|  | Major (1.5) | Minor (2.5) | Major | Minor |  |
| - Air Bubble (Terminal Bubble)- 1No. | 03 | 05 | 01 | 00 | Pass |

- Non-Conforming Modules

| Sr. No. | Module Serial No. | Defect Representation | Picture |
| --- | --- | --- | --- |
| 1. | NSME26090116839 | Air Bubble |  |

- Tests Evaluation - Dimension Check

- Non-Conforming Modules Summary

| Defect Description | Acceptance Limit |  | Observed |  | Evaluation |
| --- | --- | --- | --- | --- | --- |
|  | Major (1.5) | Minor (2.5) | Major (1.5) | Minor (2.5) |  |
| N/A | 0 | 0 | 0 | 0 | Pass |

- Non-Conforming Modules

| Sr. No. | Module Serial No. | Defect Representation | Picture |
| --- | --- | --- | --- |
| N/A | N/A | N/A | N/A |

- Photographic Records

| Front Side Picture | Back Side Picture | Label Picture (615W) |
| --- | --- | --- |
| Pallet Picture | Pallet Picture | Packing List Picture |
| Hipot Test Equipment Picture | I-V Test Equipment Picture | EL Test Equipment Picture |
| DCW, IR, GD Test | Wet Leakage Test | Length (mm) |

| Width (mm) | Diagonal (mm) | Distance Between Mounting Holes-Width Side (mm) |
| --- | --- | --- |
| Distance Between Mounting Holes-1 (mm) | Distance Between Mounting Holes-2 (mm) | Distance Between Mounting Holes-3 (mm) |
| Positive Cable Length (mm) | Negative Cable Length (mm) | Frame Height Dimension (mm) |
| Frame Width Dimension (mm) | Anodizing Thickness (μm) | Frame Wall Thickness Dimension (mm) |
| Label Picture (615W) – High Resolution |  |  |

- Tests Evaluation - Insulation Test & Ground Continuity Test

- Test Report

| Sr. No. | Module No. | DCW: 4 kV, <20 μA | IR: 1.5 kV, ≥1000 MΩ. | GND: 75A, <0.1 Ohm | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1. | NSME26090127525 | 0.9µA | 20180MΩ | 3.867mΩ | Pass |
| 2. | NSME26090117148 | 0.7µA | 13350MΩ | 1.837mΩ | Pass |
| 3. | NSME26100029457 | 1.0µA | 13370MΩ | 3.004mΩ | Pass |
| 4. | NSME26090123496 | 1.0µA | 14900MΩ | 5.381mΩ | Pass |
| 5. | NSME26100002956 | 1.0µA | 14320MΩ | 2.705mΩ | Pass |

- Photographic Records

| Sample-1 | Sample-2 | Sample-3 |
| --- | --- | --- |
| Sample-4 | Sample-5 | Machine Photo |

- Tests Evaluation - Wet Leakage Test

- Test Report

| Sr. No. | Module ID | Module Type | Applied Voltage (V) | Test Time (Sec.) | Result (≥1000MΩ) | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | NSME26100002991 | PE-132-615THGB-G12R | 1500 V | 120 Sec. | 10840MΩ | Pass |
| 2. | NSME26090117344 | PE-132-615THGB-G12R | 1500 V | 120 Sec. | 13190MΩ | Pass |
| 3. | NSME26100028671 | PE-132-615THGB-G12R | 1500 V | 120 Sec. | 11390MΩ | Pass |
| 4. | NSME26090117185 | PE-132-615THGB-G12R | 1500 V | 120 Sec. | 11520MΩ | Pass |
| 5. | NSME26090125843 | PE-132-615THGB-G12R | 1500 V | 120 Sec. | 13800MΩ | Pass |

- Photographic Records

| Sample-1 | Sample-2 | Sample-3 |
| --- | --- | --- |
| Sample-4 | Sample-5 | Wet Leakage Photo |

- Tests Evaluation - Bi-Faciality Factor

- Test Report

| Sr. No. | Module No. | Module Type | Front Side Electrical Data |  |  |  | Back Side Electrical Data |  |  |  | Pmax (80±5%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Pmax | Vpm | Ipm | FF (%) | Pmax | Vpm | Ipm | FF (%) |  |
| 1. | NSME26090117166 | PE-132-615THGB-G12R | 620.63 | 40.25 | 15.42 | 79.94 | 480.28 | 41.12 | 11.68 | 78.13 | 77.38% |
| 2. | NSME26100003753 | PE-132-615THGB-G12R | 620.63 | 40.31 | 15.40 | 80.03 | 477.61 | 41.16 | 11.61 | 78.23 | 76.95% |

- Tests Evaluation - Dynamic Mechanical Load Test

- Test Report

| Sr. No. | Module ID | Before Test (Visual) | After Test (Visual) | Before Test (Pmax) | After Test (Pmax) | Degradation (%) | Wet Leakage (≥1000MΩ) | Result |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |

- Photographic Records

| Dynamic Mechanical Load Test Set Up | Wet Leakage | DMLT Test Parameters |
| --- | --- | --- |
| N/A | N/A | N/A |

- Tests Evaluation - Static Mechanical Load Test

- Test Report

| Sr. No. | Module ID | Before Test (Visual) | After Test (Visual) | Before Test (Pmax) | After Test (Pmax) | Degradation (%) | Wet Leakage (≥1000MΩ) | Result |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |

- Photographic Records

| Static Mechanical Load Test Set Up | Wet Leakage | SMLT Test Parameters |
| --- | --- | --- |
| N/A | N/A | N/A |

- Tests Evaluation - Robustness of Termination Test

- Test Report

| Sr. No. | Module ID | Before Test (Visual) | After Test (Visual) | Before Test (Pmax) | After Test (Pmax) | Degradation (%) | Wet Leakage (≥1000MΩ) | Result |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. | NSME26090125882 | Found Ok | Found Ok | 619.78 | 617.34 | -0.393% | 12560MΩ | Pass |

- Photographic Records

| Robustness Test | Module Serial No. | Wet Leakage Result |
| --- | --- | --- |

- Tests Evaluation - Low Irradiance Test

- Test Report

| Sr. No. | Module No. | Module Type | 1000 W/m² (Pmax) |  |  |  | 200 W/m² (Pmax1) |  |  |  | (Pmax1/Pmax)*5 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Pmax | Vpm | Ipm | FF (%) | Pmax1 | Vpm | Ipm | FF (%) |  |
| 1. | NSME26090123610 | PE-132-615THGB-G12R | 620.34 | 40.22 | 15.42 | 79.89 | 121.08 | 39.97 | 3.02 | 83.78 | 97.59% |